بسم الله الرحمن الرحيم

An-najah national university

Graduation project

WELLS CONNECTING AND IMPROVING QALQILIA NETOWRK

Prepared by:

Ameer qassas

Ahmad wasef

Shareef abu zubideh

Supervised by:

Dr. ra’ed  jaber

contacts

CH1.Introduction

1.1Electrical supply

1.2 Energy consumption

1.2.1 Loads nature in qalqilia city

1.2.2 Daily load curve

1.2.3 Development of electrical

energy purchased form IEC and the growth rate:

1.3 Elements of electrical network

1.3.1 Medium voltage lines

1.3.2 Distribution transformers

CH2. Qalqelia original case network

2.1 ETAP power station

CH3. Wells study

3.1 studying the converting of wells:

3.1.1 Economic study for connecting the wells

3.2 Connecting the well

CH4. Improvements

4.1 The methods of improving:

4.1.1 Increase the swing has voltage

4.1.2 Improving using tap changing

4.1.3 Power factor improvement

4.1.4 Minimum load study

4.1.5 Optimum case

CH5. Economical study for improvement

General Introduction

The  town  of  Qalqilya  is located at the point where  the western  slops of  the  mountain  rang  of  Nablus  And  the eastern edge of  the coast of  Palestine  and  the.

And  the  eastern  edge of the coast of Palestine and the14Km of beaches Mediterranean..

And at a medium between the  settlements and Civilization  along  the Palestinian coast   and  latitude32north ,longitude 35.1 east.

The population of the city of Qalqilya is (48 thousand people )and  such a number in the  villages.

Most of  residents  of city are from  middle income class who  work  in limited   area . this  thing  compels us to talk about  costs to  citizens   for electricity

And  to tray improve the  network in the city to chive a lot of aims for us and for the city itself   .

It is known  that Palestine  is the most expensive cost in  energy  in  the region .  Palestine consumers pay about  16 cents a kwh  and this is very high cost cambered  to  other country near to Palestine  and the rate  per kilo –watt  hour of  Israeli 7 cents per kwh .

This  thing  comes  pattern  of  economic situation is  very  bad.

And  population  growth  high-level  imposes an increasing  demand  for electricity  in  the light of expansion of  architectural,  commercial and industria l  in  Palestine.

This  thing requires hard work for  TVA.

even  a  lot of problem in  the  electricity  received   to the consumers

and all this problem we will notes it in this project.

CHAPTER  ONE

Introduction

1.1 Electrical supply:

Qalqilia  electrical  distribution    network  is  fed  from  the  IEC  by  one connection  point  using a  OHL  95Mmm2.

From a substation far 1.5Km    east  of  the  city ,  and   this   substation  supplies  other   Israeli   settlements  near  to   the  city .

For  the IEC we must  know  that  the  west  bank  consumption   of energy y is  equal to  7% of IEC  Electricity  generation   which    equals   to   water   pumping   consumption   in   Israel    this give    us Abad    impression   about  the  industry  in Palestine  and the natural  of the   lodes in  Palestine   .

1.2 Energy consumption:

1.2.1 Loads nature in Qalqilia city:

The  energy  consumed is  distributed  into  different  categories   as shown  in the  table:

| Cons.% | Item |
| --- | --- |
| 76.97 | Residential |
| 16.3 | Commercial |
| 2.83 | Industry |
| 3.9 | Water pump + Light |

It    has  been   very   clear   that  the  most   consumption of  energy  in   the   residential,   and  very  small in    industry.

And   we   going  to  convert  some    water   pump   from   working   by     diesel   to   electricity   by   connected   it   to   the    network

And we  will  calculate  the   simple  bay  back   period for this converting taking into account the  yearly saving and the initial cost for this   project

1.2.2 Daily load curve:

From  a  daily  load  curve  that  we   We   brought  it  from  the municipality  Which  is    obtained  through   measurements  are   taken every   five   minutes   from the  (metering room ).

From  this  daily  load  curve  we  know    tha  t the   peak  power consumption  is   11.61 MW  and   happens  at  8:20  pm.

The periods of heavy  load    from  (10:00am-4:00pm)

And    the    average  power   consumption is  8.85  MW.

From a daily load curve   we   have  very   important  information    like:

1. max demand

2.load factor

3.the suitable distribution of the load

4.how to avoid penalties

5.total energy consumption .

and other important things

| Annual purchased M.W.H | year |
| --- | --- |
| 49650.0 | 2002 |
| 54540.0 | 2003 |
| 59220.0 | 2004 |
| 63554.0 | 2007 |
| 67589.0 | 2008 |

1.2.3 Development of electrical energy purchased from I.E.C and growth rate:

All this measurement  will  be clear in the following  table :

It  has  been  clear  that  the  energy  purchased  from  IEC   increases  each   year   and    the   total  increment  in  the  energy   consumption in  the  last  four  years  is  about   13,000 MWH

1.3   Elements of electrical network

1.3.1 Medium voltage lines:

The Over Head Lines:*

The   over   head   lines   used   in  the   network    are  22KV  , ACSR.  With   two    cross  sectional  areas  (50mm2 called rabbit,95mm2 called dog)   the    resistance /Km  and  reactance /Km  for  rabbit  and  dog  are (0.543, 0.333)    and     (0.301, 0.332)  ohm  respectively ….. and  max  current   capacity  (174A,250A)

Under ground cables:

Under  ground   cables   used  in  the  network  are

22KV  ,XLPE, 240mm2  Cu, 120mm2AL  ,95mm2AL….

-- After  dividing the network into  buses  t he transmission lines impedance have been calculated as follows:

1.3.2 Distribution Transformers:

Qalqilia  network  contains  44 22KV/0.4KV  connected  distribution

transformers with rating 400,250 KV

| Transformer ratings (Kva) | No. of transformers |
| --- | --- |
| 630 | 19 |
| 400 | 23 |
| 250 | 2 |

CHAPTER TOW:

QALQELIA ORIGENAL CASE NETWORK

2.1    ETAP Power station

By  using  etap  power  station  we  starting  the  study  with  the  original  case after  the applying the data needed

like power   factor  and  load  consumption of power  and  other  data :

The resultant basic information for Qalqelia network with out connected the well came as  shown in the following table:

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 13.759 | 6.411 | 15.179 | 90.64 |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 |
| Total Demand: | 13.759 | 6.411 | 15.179 | 90.64 |
| Total Motor Load: | 10.853 | 4.974 |  | 90.91 |
| Total Static Load: | 2.566 | 1.176 |  |  |
| Apparent Losses: | 0.341 | 0.261 |  |  |

This results shows clearly that the problem in the network not very large  for the p.f here = 90.64% and we going to increase it above 92%

All the voltage on the buses can be shown in the index, and the  the

| ID | rating | calculated | Power factor |
| --- | --- | --- | --- |
| Bus106 | 0.400 | 0.387 | 96.8 |
| Bus107 | 0.400 | 0.387 | 96.8 |
| Bus108 | 0.400 | 0.387 | 96.7 |
| Bus111 | 0.400 | 0.387 | 96.7 |
| Bus114 | 0.400 | 0.387 | 96.8 |
| Bus116 | 0.400 | 0.387 | 96.7 |
| Bus120 | 0.400 | 0.387 | 96.7 |
| Bus130 | 0.400 | 0.387 | 96.7 |
| Bus132 | 0.400 | 0.387 | 96.7 |
| Bus136 | 0.400 | 0.387 | 96.7 |
| Bus138 | 0.400 | 0.387 | 97.5 |
| Bus14 | 0.400 | 0.390 | 97.1 |
| Bus147 | 0.400 | 0.388 | 97.1 |
| Bus148 | 0.400 | 0.388 | 97.5 |
| Bus15 | 0.400 | 0.390 | 97.1 |
| Bus153 | 0.400 | 0.388 | 98.0 |
| Bus156 | 0.400 | 0.392 | 97.6 |
| Bus182 | 0.400 | 0.390 | 97.5 |
| Bus183 | 0.400 | 0.390 | 97.5 |
| Bus184 | 0.400 | 0.390 | 97.5 |
| Bus185 | 0.400 | 0.390 | 97.5 |
| Bus186 | 0.400 | 0.390 | 97.5 |
| Bus188 | 0.400 | 0.390 | 97.5 |
| Bus189 | 0.400 | 0.390 | 97.5 |
| Bus191 | 0.400 | 0.390 | 97.4 |
| Bus199 | 0.400 | 0.389 | 97.0 |
| Bus202 | 0.400 | 0.388 | 96.9 |
| Bus208 | 0.400 | 0.388 | 97.5 |
| Bus21 | 0.400 | 0.390 | 97.1 |
| Bus211 | 0.400 | 0.388 | 97.2 |
| Bus212 | 0.400 | 0.389 | 97.5 |
| Bus26 | 0.400 | 0.390 | 97.5 |
| Bus27 | 0.400 | 0.390 | 97.5 |
| Bus28 | 0.400 | 0.390 | 97.5 |
| Bus39 | 0.400 | 0.390 | 97.5 |
| Bus47 | 0.400 | 0.390 | 97.4 |
| Bus52 | 0.400 | 0.390 | 97.3 |
| Bus59 | 0.400 | 0.389 | 97.3 |
| Bus62 | 0.400 | 0.389 | 97.3 |
| Bus63 | 0.400 | 0.389 | 97.3 |
| Bus67 | 0.400 | 0.389 | 97.2 |
| Bus74 | 0.400 | 0.389 | 97.1 |
| Bus76 | 0.400 | 0.389 | 97.1 |
| Bus82 | 0.400 | 0.388 | 97.1 |
| Bus94 | 0.400 | 0.388 | 96.8 |

l-- We   notes  that   the voltage   of   buses  is not   acceptable  and this  voltage will be   less when   it reached the   consumer  and the machine and the substances for the consumer   work   the   rated   approximately  so   this     causes a lot of problem fpr the consumer

-- the percentage of losses is about 2.5 and this value and this value must be less than 2.

-- the p.f in the   network equal  90.64  and   this value causes   a lot of    problem   specially   paying   banalities   and this value  must be   (0.92-0.95)  the   p.f   is   related to    the current in the network   according that when   the p.f  is  poor  the  current in the network is high this   also can  cause  increasing the  loses in the network .

We  will notice in the improvement of the p.f     that when the p.f   increase the current   decrease  then the losses decrease.

The resultant basic information for Qalqelia network with connected the wells came as  shown in the following table:

| AMP | %PF | MVA | Mvar | MW | Bus total load (kv) | Bus |
| --- | --- | --- | --- | --- | --- | --- |
| 646.29 | 91.6 | 0.437 | 0.175 | 0.400 | 0.400 | Bus14 |
| 410.37 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus15 |
| 410.39 | 90.8 | 0.277 | 0.116 | 0.252 | 0.400 | Bus21 |
| 646.46 | 90.5 | 0.437 | 0.186 | 0.395 | 0.400 | Bus26 |
| 470.62 | 90.3 | 0.317 | 0.136 | 0.286 | 0.400 | Bus27 |
| 764.88 | 89.7 | 0.514 | 0.227 | 0.462 | 0.400 | Bus28 |
| 476.71 | 91.9 | 0.321 | 0.126 | 0.295 | 0.400 | Bus39 |
| 256.61 | 91.3 | 0.173 | 0.071 | 0.158 | 0.400 | Bus47 |
| 410.69 | 92.0 | 0.277 | 0.109 | 0.255 | 0.400 | Bus52 |
| 647.27 | 91.4 | 0.436 | 0.177 | 0.399 | 0.400 | Bus59 |
| 411.01 | 90.4 | 0.277 | 0.118 | 0.250 | 0.400 | Bus62 |
| 647.37 | 90.7 | 0.436 | 0.184 | 0.396 | 0.400 | Bus63 |
| 411.02 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus67 |
| 411.29 | 91.7 | 0.277 | 0.110 | 0.254 | 0.400 | Bus74 |
| 648.07 | 92.0 | 0.436 | 0.171 | 0.401 | 0.400 | Bus76 |
| 411.55 | 89.9 | 0.277 | 0.121 | 0.249 | 0.400 | Bus94 |
| 649.50 | 90.0 | 0.435 | 0.190 | 0.392 | 0.400 | Bus106 |
| 649.38 | 92.0 | 0.435 | 0.171 | 0.401 | 0.400 | Bus107 |
| 257.74 | 90.0 | 0.173 | 0.075 | 0.155 | 0.400 | Bus108 |
| 412.47 | 89.9 | 0.276 | 0.121 | 0.248 | 0.400 | Bus111 |
| 412.47 | 90.0 | 0.276 | 0.120 | 0.249 | 0.400 | Bus114 |
| 412.44 | 91.0 | 0.276 | 0.115 | 0.252 | 0.400 | Bus116 |
| 412.52 | 90.9 | 0.276 | 0.115 | 0.251 | 0.400 | Bus120 |
| 412.52 | 91.0 | 0.276 | 0.115 | 0.251 | 0.400 | Bus130 |
| 412.51 | 91.3 | 0.276 | 0.113 | 0.252 | 0.400 | Bus132 |
| 649.88 | 91.0 | 0.435 | 0.180 | 0.396 | 0.400 | Bus136 |
| 414.10 | 90.4 | 0.277 | 0.119 | 0.251 | 0.400 | Bus138 |
| 624.57 | 92.0 | 0.416 | 0.163 | 0.382 | 0.400 | Bus147 |
| 411.62 | 91.4 | 0.277 | 0.112 | 0.253 | 0.400 | Bus148 |
| 411.62 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus153 |
| 407.17 | 92.0 | 0.279 | 0.109 | 0.256 | 0.400 | Bus155 |
| 409.23 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus156 |
| 410.33 | 89.9 | 0.277 | 0.121 | 0.249 | 0.400 | Bus182 |
| 646.47 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus183 |
| 410.46 | 90.0 | 0.277 | 0.121 | 0.249 | 0.400 | Bus184 |
| 646.39 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus185 |
| 646.39 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus186 |
| 410.50 | 92.0 | 0.277 | 0.109 | 0.255 | 0.400 | Bus188 |
| 476.66 | 91.4 | 0.321 | 0.130 | 0.293 | 0.400 | Bus189 |
| 476.77 | 91.6 | 0.321 | 0.129 | 0.294 | 0.400 | Bus191 |
| 647.02 | 89.9 | 0.436 | 0.191 | 0.392 | 0.400 | Bus199 |
| 411.77 | 90.0 | 0.277 | 0.121 | 0.249 | 0.400 | Bus202 |
| 412.04 | 92.0 | 0.277 | 0.108 | 0.254 | 0.400 | Bus208 |
| 411.62 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus211 |

The result of basic information of the network with connected wells came as shown :

| %PF | MVA | Mvar | MW |  |
| --- | --- | --- | --- | --- |
| 90.65 lagging | 15.706 | 6.631 | 14.237 | Swing Bus(es): |
| 100.00 lagging | 0.000 | 0.000 | 0.000 | Generators: |
| 90.65 lagging | 15.706 | 6.631 | 14.237 | Total Demand: |
| 90.93 lagging | 12.438 | 5.176 | 11.310 | Total Motor Load: |
|  |  | 1.174 | 2.561 | Total Static Load: |
|  |  | 0.281 | 0.366 | Apparent Losses: |
|  |  | 0.000 | 0.000 | System Mismatch: |

CHEPTER THREE

WELLS

3.1 STUDING THE CONVERTING OF WELLS:

3.1.1 Economical study for connecting the wells

Qalqilya  city   has  about   33   Tub well   Some  of  them are   privately owned  by  the  city's  population  and the    others  Owned   by    the municipality.

The  municipality    tub wells   water   pumps are    converted

From diesel to electricity by connected them on the network . And in this project we are going to convert some of diesel water pump to electricity in this project.

We will going to  show all   the information  about the wells that wanted to to converted in the following table:

| The name of the well | Diesel consumption | Working hours | Daily m3 | Pumping altitude |
| --- | --- | --- | --- | --- |
| Alquba A | 6 L \ hour | 30 \ month | 45 m3 | 20 m |
| Alquba B | 7 L \ hour | 100 \ month | 84 m3 | 20 m |
| Abu olby | 18 L \ hour | 140h \ month | 85 m3 | 60 m |
| Mohammad saeed | 18 L \ hour | 80h \ month | 72 m3 | 50 m |
| Wadea hoseen | 12 L \ hour | 70h \ month | 72 m3 | 55 m |
| Abd alsalam | 9 L \ hour | 80h \ month | 60 m3 | 50 m |
| Saleh saeed | 6 L \ hour | 60h \ month | 55 m3 | 40 m |

From this data  we can calculate all the measurement needed  to converting the well.

Firstely  we   wont to  calculate  the   daily  and  the  monthly  and  yearly consumption   of diesel    for each tubewell

As   the   following   table:

| Annual consumption of diesel(liter/year) | Monthly consumption of diesel(liter/mth) | Daily consumption of diesel(liter/day) | Well name |
| --- | --- | --- | --- |
| 2160 | 180 | 6 | Al Qobaa A 33 KW |
| 8388 | 699 | 23.3 | AL Qobaa B 67 KW |
| 30240 | 2520 | 84 | Abu Olba 93.25 KW |
| 17280 | 1440 | 48 | Mohammad Seed 119.3KW |
| 10080 | 840 | 28 | Wdeea Hasanean 37.3KW |
| 8640 | 720 | 24 | Abd AL Salam 37.3KW |
| 4320 | 360 | 12 | Saleh AL saead 37.3KW |

After  this  table  we  need  to  calcoulate   the  total  annual  cost  for  each well which  consist  from  two  part  the  running  cost  and  the  fixed  cost.

Running    cost   consist   of    diesel  yearly    cost   and    annual maintenance   cost   which   consist of  tow   part  :

The  first  part  is  annual  electrical  maintenance  which reach   about 300$  for  each pump .

The  second  part is   the  oil   consumption   which  reach about 640$ for each water  pump .

This   about   running cost  ,but  the fixed   cost    of the water   pump consist    of the capital   cost of the water   pump which  reach about 600$ for 1 KW

Multiplied   by the depreciation  factor    which reach about   (0.08-0.12) these   calculation   for each well in the table below:

| Total cost ($) | Fixed Annual cost ($) | Annual running cost($) | The annual cost of diesel($) | The annual cost of operating wells |
| --- | --- | --- | --- | --- |
| 6059.2 | 1980 | 4079.2 | 3139.2 | Al Qobaa A |
| 17150.56 | 4020 | 13130.56 | 12190.56 | AL Qobaa B |
| 50483.8 | 5595 | 44888.8 | 43948.8 | Abu Olba |
| 33211 | 7158 | 26053.6 | 25113.6 | Mohammad Seed |
| 17827 | 2238 | 15589.6 | 14649.6 | Wdeea Hasanean |
| 15734.8 | 2238 | 13496.8 | 12556.8 | Abd AL Salam |
| 9453 | 2238 | 7215 | 6275 | Saleh AL saead |

All   these c  alculation   in  order   to know the   Cost/Kwh

Which    can be   find by   this equation below:

Cost/Kwh = (Total Annual Cost)/(Total Energy Consumption)

This low give   the cost of kwh in $   where:

Total    Annual   Cost = Running   cos t +  Fixed cost

Total   Energy  Consumption :  which mean the total energy produced from  the diesel   where the  liter  of diesel   produce 3.2 Kwh.

So total   energy  consumption=    diesel   yearly   consumption    in  liter * 3.2kwh

All these calculation done in the table in the next bage:

| Cost /Kwh ($) | Total energy consumption For pump ($) | Well name |
| --- | --- | --- |
| 0.876 | 6912 | Al Qobaa A |
| 0.638 | 26841.6 | AL Qobaa B |
| 0.521 | 96768 | Abu Olba |
| 0.6 | 55296 | Mohammad Seed |
| 0.552 | 32256 | Wdeea Hasanean |
| 0.569 | 27648 | Abd AL Salam |
| 0.683 | 13824 | Saleh AL saead |

This  is  all  thing   about  the  water  pump  opereating   in  diesel    we go  know  to  see   the   opereation   of this   pump  in  electricity  and  to see the  deference   about the  two  operation:

Firstly   we  need  calculate   the  total   energy   consumption  by   each pump   by  using   the   equation   below:

E= Q *H *9.81 *η

Where:

E : Energy  consumption  (Wh/day).

Q:  the   amount  of pumping  ( m3 /day).

H:  the   high   of   flow

η   : the efficiency of the motor  (0.4).

in  the  table below we show  the  annual  energy  consumptions   :

| Annual energy consumption (kwh) | E (Kwh/day) | The name of well |
| --- | --- | --- |
| 1281.39 | 3.53 | Al Qobaa A 33.57 KW |
| 2392.17 | 6.59 | Al Qobaa B 67.14 KW |
| 7260 | 20 | Abu Olba 93.25 KW |
| 5125.56 | 14,12 | Mohammad Seed 119.3 KW |
| 5626.5 | 15.5 | Wadee Hasan 37.3 KW |
| 4273.2 | 11.77 | Abd Al salam 37.3 KW |
| 3133.4 | 8.6328 | Saleh Al Seed 37.3 KW |

After   we  calculate  the  annual  energy consumed  by  the   motor

We   going  to  calculate  the  total cost  which e  qual

=  running cost  +  fixed cost

running   cost   =  the  cost of   energy   consumption  , we take   the cost of  kwh    0.6 IS so we done the   equ. (0.6 * E ) / 3.75

to   have   the  cost  in  $

the  fixed  cost  =    fees  *  depreciation  factor  (0.1)

fees   =  The   #  of  ampere  *   22

where the # of ampere for each pump is slandered value from the  company .

the fess for each ampere from the amicability = 22$.

in   the  table  below  we  show  the total  annual cost in $:

| Total annual cost in $ | Capital cost In $ | Running cost In $ | The name of well |
| --- | --- | --- | --- |
| 337.1 | 132.08 | 205.02 | Al Qobaa A 60 A |
| 785.3 | 402.6 | 382.7 | AL Qobaa B 183 A |
| 1564.2 | 402.6 | 1161.6 | Abu Elba 183 A |
| 1260 | 440 | 820 | Mohammad Seed 200A |
| 1043 | 143 | 900 | Wdee Hasan 65A |
| 826.7 | 143 | 683.7 | Abd Al Salam 65A |
| 644 | 143 | 501.33 | Saleh Al Seed 65A |

After the   last   table  of the   annual   total   cost we   going   to calculate  the  cost / kwh

Cost /kwh = total annual cost /E

The following table show this calculation:

| Cost / kwh $ | Name of well |
| --- | --- |
| 0.263 | Al Qobaa A |
| 0.328 | Al Qobaa B |
| 0.215 | Abu elba |
| 0.245 | Mohammad Seed |
| 0.185 | Wadee Hasan |
| 0.193 | Abd al salam |
| 0.206 | Saleh al seed |

From   the   last table    it has been very   clear   that   the    electricity

Is    more    economic   than   the   diesel    operation      this has been clear

From   the   previous calculation of the   cost/kwh

Now we going to show the economical  study for the well

The   cost   of converting   the   pump   to run on the   network      can be calculated   from the   fees that   bayed to    the amicability for each     ampere wonted ,   and   we mention    before the cost of   fees for one    ampere is   about   22$   and   this will   be    more clear    by this     equation :

The    cost    = 60 * 22 + 183 * 22 +183 * 22 + 200 * 22 +65 * 22

+ 65 * 22 + 65 * 22 = 18062 $

this is the cost needed to convert the wells.

All   this   for  running the   well     at   electricity  .

For   diesel   operation :

The   yearly   diesel   consumption   by    the   wells   in   litter :

= 2160 + 8388 +30240  + 17280 + 10080

+8640 + 4320 = 181108 litter of diesel .

And  at   the  same  operation  of   diesel    we    want    to

calculate the   total  cost  of   running  the  well  consist   ( diesel

consumption  , maintenance   and oil yearly ):

this = 4079.2 + 13130.56 + 44888.8 + 26053.6 +

15589.6 + 13496.8 + 7215 = 124453.56 $ .

The   total   kwh   will    be    needed    by   the   pump   which calculated  for   each   well  by the  equ.

E = Q * 9.8 * H *η   which   mentioned   before

That    give    the daily   energy   consumption   in  kwh    and

By    multiplying   this   by   #   of days in the year , the annual energy consumption = 1281.39 + 2392.17 + 7260 +

5125.56 + 5626.5 + 4273.2 + 3133.4 = 29092.22 kwh

-the  the     cost /kwh = .6 sh in $ = 0.6 /3.75 =0.16 $

So     the   total   annual cost = 29092.22*0.16 =  4654.7 $

the simple Pay back period will be due to the net cash flow shown :

this   CF   Show   the   investment   and   the  annual  saving  and  to

calculate the simple Pay back period  we use this equ.:

S.P.B.P   =   initial investment /  annual saving

= 18062/119799 = 0.151 year

And   this  = 0.151 * 365 = 55.2 day

And    pay    back   period   ( by taken the time value of money  )   and

The  interest rat = 10%  can   be   calculated  by  this  equ.   P  =

A(P/A,I% , n) where:

P : the initial investment .

A : annual saving .

I  : interest rat.

n. : number of years

.

And by solving this equ.

( P/A,10%,n) = 1.8 .

from the table n = 2 month

- from   this    calculation  we notes  that   it  is   a logic  period to recover   our   investment .

- notes that we did not need any transformers .

- and   we   must  notes  that  the   cost of  cables   and   other

Substances  needed  to  the  connecting   is covered  by the

Municipality.

3.2 Connecting the well:

Adding   wells   pump   to   the   network   by   connected  on   the  network  and   in   our    project   we   connected   it   directly    to   an existed     transformer  near  to  the  location  of    the wells ,  the 7 wells here  Is connected  to the  transformer  and  buses  as shown in the  following table:

| Name of well | # of bus |
| --- | --- |
| Al Qoba A | 27 |
| Al Qoba B | 28 |
| Abu elba | 82 |
| Mohammad Saeed | 147 |
| Wadee Hassan | 39 |
| Abd Alsalam | 191 |
| Saleh Alseed | 189 |

And after  doing  run  to  the  network  at  etab  program  we get  the  following   :

The result of basic information of the network :

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 14.237 | 6.631 | 15.706 | 90.65 |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 |
| Total Demand: | 14.237 | 6.631 | 15.706 | 90.65 |
| Total Motor Load: | 11.310 | 5.176 | 12.438 | 90.93 |
| Total Static Load: | 2.561 | 1.174 |  |  |
| Apparent Losses: | 0.366 | 0.281 |  |  |
| System Mismatch: | 0.000 | 0.000 |  |  |

From  the  previous  table  we  note  that  after  we  connected  the  wells  the total power increase  and the apparent losses also increase

All  the  voltage  on  the buses can be shown in the following  table :

| ID | Rating | Calculated | P.F |
| --- | --- | --- | --- |
| Bus106 | 0.400 | 0.387 | 96.7 |
| Bus107 | 0.400 | 0.387 | 96.8 |
| Bus108 | 0.400 | 0.387 | 96.7 |
| Bus111 | 0.400 | 0.387 | 96.7 |
| Bus114 | 0.400 | 0.387 | 96.7 |
| Bus116 | 0.400 | 0.387 | 96.7 |
| Bus120 | 0.400 | 0.387 | 96.7 |
| Bus130 | 0.400 | 0.387 | 96.7 |
| Bus132 | 0.400 | 0.387 | 96.7 |
| Bus136 | 0.400 | 0.387 | 96.7 |
| Bus138 | 0.400 | 0.387 | 96.7 |
| Bus14 | 0.400 | 0.390 | 97.5 |
| Bus147 | 0.400 | 0.384 | 96.0 |
| Bus148 | 0.400 | 0.388 | 97.0 |
| Bus15 | 0.400 | 0.390 | 97.5 |
| Bus153 | 0.400 | 0.388 | 97.0 |
| Bus156 | 0.400 | 0.392 | 98.0 |
| Bus182 | 0.400 | 0.390 | 97.5 |
| Bus183 | 0.400 | 0.390 | 97.5 |
| Bus184 | 0.400 | 0.390 | 97.5 |
| Bus185 | 0.400 | 0.390 | 97.5 |
| Bus186 | 0.400 | 0.390 | 97.5 |
| Bus188 | 0.400 | 0.390 | 97.5 |
| Bus189 | 0.400 | 0.389 | 97.2 |
| Bus191 | 0.400 | 0.389 | 97.1 |
| Bus199 | 0.400 | 0.389 | 97.3 |
| Bus202 | 0.400 | 0.388 | 97.0 |
| Bus208 | 0.400 | 0.388 | 96.9 |
| Bus21 | 0.400 | 0.390 | 97.5 |
| Bus211 | 0.400 | 0.388 | 97.0 |
| Bus212 | 0.400 | 0.389 | 97.2 |
| Bus26 | 0.400 | 0.390 | 97.5 |
| Bus27 | 0.400 | 0.389 | 97.2 |
| Bus28 | 0.400 | 0.388 | 97.1 |
| Bus39 | 0.400 | 0.389 | 97.1 |
| Bus47 | 0.400 | 0.390 | 97.4 |
| Bus52 | 0.400 | 0.390 | 97.4 |
| Bus59 | 0.400 | 0.389 | 97.3 |
| Bus62 | 0.400 | 0.389 | 97.3 |
| Bus63 | 0.400 | 0.389 | 97.3 |
| Bus67 | 0.400 | 0.389 | 97.3 |
| Bus74 | 0.400 | 0.389 | 97.2 |
| Bus76 | 0.400 | 0.388 | 97.1 |
| Bus82 | 0.400 | 0.386 | 96.5 |
| Bus94 | 0.400 | 0.388 | 97.1 |

After  this   table   we  can  see  that  the  wells does  not  affected   in large   scale   to the   network    And   the   problems is   stile the   same before    but it   is   increase in small   scale and   we   going   to   solve all   this   problem   in   the improvement    in   the   next     chapter.

CHAPTER FOUR

IMPROVEMETS

4.1 The methods of improving

we have # of methods in order to improve the network  for  a lot of positive effects  such as  reducing the cost / kwh  . these methods are :

1-  increasing  the  swing  bus  voltage   .

2-  tab changing in the transformer.

3- adding capacitors to produce reactive power .

4- change the connection of the network.

4.1.1 Increase the swing bus voltage :

In   the   network   the   connection  point   have   the   flexibility   to increase   the   voltage    on   the   swing   bus   up to 5%   from   the original   voltage   (22 kv)  the   new  value   of   the   swing   bus voltage   equal   23.1   the   run   of  etab   after   applying   this improvement   the data   shown in the following table:

| ID | Rating | Calculated | P.F |
| --- | --- | --- | --- |
| Bus106 | 0.400 | 0.404 | 96.7 |
| Bus107 | 0.400 | 0.412 | 96.8 |
| Bus108 | 0.400 | 0.419 | 96.7 |
| Bus111 | 0.400 | 0.412 | 96.7 |
| Bus114 | 0.400 | 0.412 | 96.7 |
| Bus116 | 0.400 | 0.412 | 96.7 |
| Bus120 | 0.400 | 0.419 | 96.7 |
| Bus130 | 0.400 | 0.419 | 96.7 |
| Bus132 | 0.400 | 0.412 | 96.7 |
| Bus136 | 0.400 | 0.412 | 96.7 |
| Bus138 | 0.400 | 0.419 | 96.7 |
| Bus14 | 0.400 | 0.412 | 97.5 |
| Bus147 | 0.400 | 0.412 | 96.0 |
| Bus148 | 0.400 | 0.412 | 97.0 |
| Bus15 | 0.400 | 0.412 | 97.5 |
| Bus153 | 0.400 | 0.412 | 97.0 |
| Bus156 | 0.400 | 0.411 | 98.0 |
| Bus182 | 0.400 | 0.411 | 97.5 |
| Bus183 | 0.400 | 0.411 | 97.5 |
| Bus184 | 0.400 | 0.410 | 97.5 |
| Bus185 | 0.400 | 0.410 | 97.5 |
| Bus186 | 0.400 | 0.390 | 97.5 |
| Bus188 | 0.400 | 0.412 | 97.5 |
| Bus189 | 0.400 | 0.412 | 97.2 |
| Bus191 | 0.400 | 0.412 | 97.1 |
| Bus199 | 0.400 | 0.412 | 97.3 |
| Bus202 | 0.400 | 0.412 | 97.0 |
| Bus208 | 0.400 | 0.412 | 96.9 |
| Bus21 | 0.400 | 0.412 | 97.5 |
| Bus211 | 0.400 | 0.411 | 97.0 |
| Bus212 | 0.400 | 0.411 | 97.2 |
| Bus26 | 0.400 | 0.411 | 97.5 |
| Bus27 | 0.400 | 0.411 | 97.2 |
| Bus28 | 0.400 | 0.419 | 97.1 |
| Bus39 | 0.400 | 0.412 | 97.1 |
| Bus47 | 0.400 | 0.412 | 97.4 |
| Bus52 | 0.400 | 0.412 | 97.4 |
| Bus59 | 0.400 | 0.412 | 97.3 |
| Bus62 | 0.400 | 0.412 | 97.3 |
| Bus63 | 0.400 | 0.412 | 97.3 |
| Bus67 | 0.400 | 0.412 | 97.3 |
| Bus74 | 0.400 | 0.412 | 97.2 |
| Bus76 | 0.400 | 0.419 | 97.1 |
| Bus82 | 0.400 | 0.413 | 96.5 |
| Bus94 | 0.400 | 0.412 | 97.1 |

This   table   shows   the   bus voltage  after   increasing  the  swing  bus voltage.

And  it  can  be  clear  that the  voltage of the   buses  increased  to   give   the   consumer   the   rated   voltage .

4.1.2   Improving using tap changing:

In this   method   of  tab   changing    involves   changing    in  the   tab ratio  on t he transformer    but in   limiting   rang   which not   accede (5% ).

And   after   we   applying   this   method   we   have the following   result   as  shown  I  the  table   below :

| AMP | %PF | MVA | Mvar | MW | Bus total load (kv) | Bus |
| --- | --- | --- | --- | --- | --- | --- |
| 642.32 | 91.6 | 0.438 | 0.176 | 0.402 | 0.400 | Bus14 |
| 407.84 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus15 |
| 413.06 | 90.8 | 0.276 | 0.116 | 0.251 | 0.400 | Bus21 |
| 642.49 | 90.5 | 0.438 | 0.186 | 0.397 | 0.400 | Bus26 |
| 467.49 | 90.3 | 0.318 | 0.137 | 0.287 | 0.400 | Bus27 |
| 759.71 | 89.7 | 0.516 | 0.228 | 0.463 | 0.400 | Bus28 |
| 473.52 | 91.9 | 0.322 | 0.127 | 0.296 | 0.400 | Bus39 |
| 258.28 | 91.3 | 0.173 | 0.070 | 0.158 | 0.400 | Bus47 |
| 408.17 | 92.0 | 0.278 | 0.109 | 0.256 | 0.400 | Bus52 |
| 651.50 | 91.4 | 0.435 | 0.176 | 0.397 | 0.400 | Bus59 |
| 408.48 | 90.4 | 0.278 | 0.119 | 0.251 | 0.400 | Bus62 |
| 643.38 | 90.7 | 0.438 | 0.184 | 0.397 | 0.400 | Bus63 |
| 413.70 | 91.0 | 0.276 | 0.114 | 0.251 | 0.400 | Bus67 |
| 408.75 | 91.7 | 0.278 | 0.111 | 0.255 | 0.400 | Bus74 |
| 644.07 | 92.0 | 0.438 | 0.172 | 0.403 | 0.400 | Bus76 |
| 809.04 | 91.6 | 0.547 | 0.220 | 0.501 | 0.400 | Bus82 |
| 414.25 | 89.9 | 0.276 | 0.121 | 0.248 | 0.400 | Bus94 |
| 653.77 | 90.0 | 0.434 | 0.189 | 0.390 | 0.400 | Bus106 |
| 653.64 | 92.0 | 0.434 | 0.170 | 0.399 | 0.400 | Bus107 |
| 259.43 | 90.0 | 0.172 | 0.075 | 0.155 | 0.400 | Bus108 |
| 415.18 | 89.9 | 0.275 | 0.121 | 0.247 | 0.400 | Bus111 |
| 415.18 | 90.0 | 0.275 | 0.120 | 0.248 | 0.400 | Bus114 |
| 415.16 | 91.0 | 0.275 | 0.114 | 0.251 | 0.400 | Bus116 |
| 409.96 | 90.9 | 0.277 | 0.116 | 0.252 | 0.400 | Bus120 |
| 409.96 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus130 |
| 415.22 | 91.3 | 0.275 | 0.112 | 0.251 | 0.400 | Bus132 |
| 654.16 | 91.0 | 0.433 | 0.180 | 0.394 | 0.400 | Bus136 |
| 411.54 | 90.4 | 0.278 | 0.119 | 0.252 | 0.400 | Bus138 |
| 619.88 | 92.0 | 0.417 | 0.163 | 0.383 | 0.400 | Bus147 |
| 409.08 | 91.4 | 0.278 | 0.113 | 0.254 | 0.400 | Bus148 |
| 409.08 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus153 |
| 404.69 | 92.0 | 0.280 | 0.110 | 0.257 | 0.400 | Bus155 |
| 406.73 | 91.0 | 0.279 | 0.116 | 0.254 | 0.400 | Bus156 |
| 407.81 | 89.9 | 0.278 | 0.122 | 0.250 | 0.400 | Bus182 |
| 642.50 | 90.0 | 0.438 | 0.191 | 0.394 | 0.400 | Bus183 |
| 407.94 | 90.0 | 0.278 | 0.121 | 0.250 | 0.400 | Bus184 |
| 642.42 | 90.0 | 0.438 | 0.191 | 0.395 | 0.400 | Bus185 |
| 642.42 | 90.0 | 0.438 | 0.191 | 0.395 | 0.400 | Bus186 |
| 407.98 | 92.0 | 0.278 | 0.109 | 0.256 | 0.400 | Bus188 |
| 473.47 | 91.4 | 0.322 | 0.131 | 0.294 | 0.400 | Bus189 |
| 480.17 | 91.6 | 0.320 | 0.128 | 0.293 | 0.400 | Bus191 |
| 643.04 | 89.9 | 0.438 | 0.192 | 0.394 | 0.400 | Bus199 |
| 409.22 | 90.0 | 0.278 | 0.121 | 0.250 | 0.400 | Bus202 |
| 409.49 | 92.0 | 0.278 | 0.109 | 0.255 | 0.400 | Bus208 |
| 409.08 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus211 |
| 408.75 | 91.7 | 0.278 | 0.111 | 0.255 | 0.400 | Bus212 |

This table show that the volteges of buses after improvement by changing the taps of transformer.

| % PF | MVA | Mvar | MW |  |
| --- | --- | --- | --- | --- |
| 90.65 | 15.732 | 6.643 | 14.261 | Swing Bus(es): |
| 100.00 | 0.000 | 0.000 | 0.000 | Generators: |
| 90.65 | 15.732 | 6.643 | 14.261 | Total Demand: |
| 90.93 | 12.438 | 5.176 | 11.310 | Total Motor Load: |
|  |  | 1.183 | 2.582 | Total Static Load: |
|  |  | 0.283 | 0.369 | Apparent Losses: |
|  |  | 0.000 | 0.000 | System Mismatch: |

Representing the total demand….. losses ,and whole PF  for the tap changing improvement.

4.1.3 Power factor improvement:

--our  aim   to   improvement   of  p .f   in  order  to  avoid  penalties  and to  reduce   the current    flow   in the network    which   reduce   the electrical   losses   in  the network

-- the power   factor   after  the   improving   must   be   in the   range (0.92- 0.95)

-- we   use   this   equation   to   calculate   the   reactive   power

Needing  for  this  improvement  is:

Qc  = P(tan cos(p.f old)- tan cos (p.f new))

Pf old= 90.65

Pf new at least =92%

Q= 14.237 (tan(cos(0.9065) – tan (cos (0.92))

Q= 566.6

Approximation = 600 kvr

By  adding   these  capacitor  to yhe network   we  add  the capacitor   bank 3

Capacitor  then   to  the  bus  which  have   minimum  p.f  and  the  capacitors is

added in  delta connection  :

Parallel   to  the  transformer in the secondary side as shown in the table

Below:

| Bus number | Capacitor needed |
| --- | --- |
| 39 | 200 kvr |
| 183 | 200 kvr |
| 28 | 200kvr |

After adding these capacitor bank and appling these information to the network we notice the following table :

Buss voltages after adding capacitance bank

| AMP | %PF | MVA | Mvar | MW | Bus total load | Bus |
| --- | --- | --- | --- | --- | --- | --- |
| 646.25 | 91.6 | 0.437 | 0.175 | 0.400 | 0.400 | Bus14 |
| 410.34 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus15 |
| 410.36 | 90.8 | 0.277 | 0.116 | 0.252 | 0.400 | Bus21 |
| 646.41 | 90.5 | 0.437 | 0.186 | 0.395 | 0.400 | Bus26 |
| 470.57 | 90.3 | 0.317 | 0.136 | 0.286 | 0.400 | Bus27 |
| 739.83 | 92.4 | 0.501 | 0.192 | 0.463 | 0.400 | Bus28 |
| 503.19 | 86.5 | 0.342 | 0.171 | 0.296 | 0.400 | Bus39 |
| 256.58 | 91.3 | 0.173 | 0.071 | 0.158 | 0.400 | Bus47 |
| 410.67 | 92.0 | 0.277 | 0.109 | 0.255 | 0.400 | Bus52 |
| 647.23 | 91.4 | 0.436 | 0.177 | 0.399 | 0.400 | Bus59 |
| 410.98 | 90.4 | 0.277 | 0.118 | 0.250 | 0.400 | Bus62 |
| 647.33 | 90.7 | 0.436 | 0.184 | 0.396 | 0.400 | Bus63 |
| 410.99 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus67 |
| 411.25 | 91.7 | 0.277 | 0.110 | 0.254 | 0.400 | Bus74 |
| 648.01 | 92.0 | 0.436 | 0.171 | 0.401 | 0.400 | Bus76 |
| 814.64 | 91.6 | 0.545 | 0.219 | 0.499 | 0.400 | Bus82 |
| 411.51 | 89.9 | 0.277 | 0.121 | 0.249 | 0.400 | Bus94 |
| 649.41 | 90.0 | 0.435 | 0.190 | 0.392 | 0.400 | Bus106 |
| 649.29 | 92.0 | 0.435 | 0.171 | 0.401 | 0.400 | Bus107 |
| 257.70 | 90.0 | 0.173 | 0.075 | 0.155 | 0.400 | Bus108 |
| 412.41 | 89.9 | 0.276 | 0.121 | 0.248 | 0.400 | Bus111 |
| 412.41 | 90.0 | 0.276 | 0.120 | 0.249 | 0.400 | Bus114 |
| 412.38 | 91.0 | 0.276 | 0.115 | 0.252 | 0.400 | Bus116 |
| 412.45 | 90.9 | 0.276 | 0.115 | 0.251 | 0.400 | Bus120 |
| 412.46 | 91.0 | 0.276 | 0.115 | 0.252 | 0.400 | Bus130 |
| 412.44 | 91.3 | 0.276 | 0.113 | 0.252 | 0.400 | Bus132 |
| 649.77 | 91.0 | 0.435 | 0.180 | 0.396 | 0.400 | Bus136 |
| 447.11 | 83.2 | 0.302 | 0.168 | 0.252 | 0.400 | Bus138 |
| 624.50 | 92.0 | 0.416 | 0.163 | 0.382 | 0.400 | Bus147 |
| 411.58 | 91.4 | 0.277 | 0.112 | 0.253 | 0.400 | Bus148 |
| 411.59 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus153 |
| 407.17 | 92.0 | 0.279 | 0.109 | 0.256 | 0.400 | Bus155 |
| 409.23 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus156 |
| 410.30 | 89.9 | 0.277 | 0.121 | 0.249 | 0.400 | Bus182 |
| 646.43 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus183 |
| 410.43 | 90.0 | 0.277 | 0.121 | 0.250 | 0.400 | Bus184 |
| 646.35 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus185 |
| 646.35 | 90.0 | 0.437 | 0.190 | 0.393 | 0.400 | Bus186 |
| 410.47 | 92.0 | 0.277 | 0.109 | 0.255 | 0.400 | Bus188 |
| 476.62 | 91.4 | 0.321 | 0.130 | 0.293 | 0.400 | Bus189 |
| 476.72 | 91.6 | 0.321 | 0.129 | 0.294 | 0.400 | Bus191 |
| 646.98 | 89.9 | 0.436 | 0.191 | 0.392 | 0.400 | Bus199 |
| 411.73 | 90.0 | 0.277 | 0.121 | 0.249 | 0.400 | Bus202 |
| 411.99 | 92.0 | 0.277 | 0.108 | 0.254 | 0.400 | Bus208 |
| 411.59 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus211 |
| 411.25 | 91.7 | 0.277 | 0.110 | 0.254 | 0.400 | Bus212 |

The result of basic information of the network after adding capacitance :

| %PF | MVA | Mvar | MW |  |
| --- | --- | --- | --- | --- |
| 92.02 lagging | 15.468 | 6.054 | 14.234 | Swing buses |
| 100.00 lagging | 0.000 | 0.000 | 0.000 | Generator |
| 92.02 lagging | 15.468 | 6.054 | 14.234 | Total demand |
|  |  | 0.601 | 2.564 | Total static load |
|  |  | 0.277 | 0.360 | Apparent losses |
|  |  | 0.000 | 0.000 | System mismatch |

We notice that:

the PF was improved from 90% to 92%

apparent power was decrease from .366 to .360

4.1.4   Minimum load study

At this case we will study the network of qalqilia  at minimum load , as we know that the network not always work at full load there will be time that the network loads will be 30 % form the original load .

This case can be easy study by assuming every load is 30 % from the original value of it and by applying these changing to the E tap and the result will be:

Result of minimum load :

| AMP | %PF | MVA | Mvar | MW | BUS TOTAL LOAD (KV) | Bus |
| --- | --- | --- | --- | --- | --- | --- |
| 192.83 | 91.6 | 0.133 | 0.053 | 0.121 | 0.400 | Bus14 |
| 121.79 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus15 |
| 121.79 | 90.8 | 0.084 | 0.035 | 0.076 | 0.400 | Bus21 |
| 192.84 | 90.5 | 0.133 | 0.056 | 0.120 | 0.400 | Bus26 |
| 139.31 | 90.3 | 0.096 | 0.041 | 0.086 | 0.400 | Bus27 |
| 227.73 | 89.7 | 0.156 | 0.069 | 0.140 | 0.400 | Bus28 |
| 140.79 | 91.9 | 0.097 | 0.038 | 0.089 | 0.400 | Bus39 |
| 76.85 | 91.3 | 0.053 | 0.022 | 0.048 | 0.400 | Bus47 |
| 121.81 | 92.0 | 0.084 | 0.033 | 0.077 | 0.400 | Bus52 |
| 192.92 | 91.4 | 0.133 | 0.054 | 0.121 | 0.400 | Bus59 |
| 121.84 | 90.4 | 0.084 | 0.036 | 0.076 | 0.400 | Bus62 |
| 192.92 | 90.7 | 0.133 | 0.056 | 0.120 | 0.400 | Bus63 |
| 193.32 | 91.0 | 0.132 | 0.055 | 0.120 | 0.400 | Bus67 |
| 121.86 | 91.7 | 0.084 | 0.033 | 0.077 | 0.400 | Bus74 |
| 192.98 | 92.0 | 0.133 | 0.052 | 0.122 | 0.400 | Bus76 |
| 241.27 | 91.6 | 0.165 | 0.066 | 0.151 | 0.400 | Bus82 |
| 121.89 | 89.9 | 0.084 | 0.037 | 0.075 | 0.400 | Bus94 |
| 193.10 | 90.0 | 0.132 | 0.058 | 0.119 | 0.400 | Bus106 |
| 193.09 | 92.0 | 0.132 | 0.052 | 0.122 | 0.400 | Bus107 |
| 76.95 | 90.0 | 0.053 | 0.023 | 0.048 | 0.400 | Bus108 |
| 121.96 | 89.9 | 0.084 | 0.037 | 0.075 | 0.400 | Bus111 |
| 121.96 | 90.0 | 0.084 | 0.036 | 0.075 | 0.400 | Bus114 |
| 121.96 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus116 |
| 121.97 | 90.9 | 0.084 | 0.035 | 0.076 | 0.400 | Bus120 |
| 121.97 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus130 |
| 121.96 | 91.3 | 0.084 | 0.034 | 0.076 | 0.400 | Bus132 |
| 193.13 | 91.0 | 0.132 | 0.055 | 0.121 | 0.400 | Bus136 |
| 121.97 | 90.4 | 0.084 | 0.036 | 0.076 | 0.400 | Bus138 |
| 183.41 | 92.0 | 0.126 | 0.049 | 0.116 | 0.400 | Bus147 |
| 121.89 | 91.4 | 0.084 | 0.034 | 0.077 | 0.400 | Bus148 |
| 121.89 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus153 |
| 121.51 | 92.0 | 0.084 | 0.033 | 0.077 | 0.400 | Bus155 |
| 121.69 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus156 |
| 121.79 | 90.0 | 0.084 | 0.037 | 0.075 | 0.400 | Bus184 |
| 192.84 | 90.0 | 0.133 | 0.058 | 0.119 | 0.400 | Bus185 |
| 192.84 | 90.0 | 0.133 | 0.058 | 0.119 | 0.400 | Bus186 |
| 121.80 | 92.0 | 0.084 | 0.033 | 0.077 | 0.400 | Bus188 |
| 140.78 | 91.4 | 0.097 | 0.039 | 0.088 | 0.400 | Bus189 |
| 140.79 | 91.6 | 0.097 | 0.039 | 0.089 | 0.400 | Bus191 |
| 192.89 | 89.9 | 0.133 | 0.058 | 0.119 | 0.400 | Bus199 |
| 121.90 | 90.0 | 0.084 | 0.036 | 0.075 | 0.400 | Bus202 |
| 121.93 | 92.0 | 0.084 | 0.033 | 0.077 | 0.400 | Bus208 |
| 121.89 | 91.0 | 0.084 | 0.035 | 0.076 | 0.400 | Bus211 |
| 121.86 | 91.7 | 0.084 | 0.033 | 0.077 | 0.400 | Bus212 |

We notice that

All voltage of this case is high since there is less current go throw the wire and so the voltage drop will be less .

| %PF | MVA | Mvar | MW |  |
| --- | --- | --- | --- | --- |
| 90.84 lagging | 4.711 | 1.970 | 4.280 | Swing Bus(es): |
| 100.00 lagging | 0.000 | 0.000 | 0.000 | Generators: |
| 90.84 lagging | 4.711 | 1.970 | 4.280 | Total Demand: |
| 90.93 lagging | 3.779 | 1.573 | 3.436 | Total Motor Load: |
|  |  | 0.372 | 0.811 | Total Static Load: |
|  |  | 0.025 | 0.033 | Apparent Losses: |
|  |  | 0.000 | 0.000 | System Mismatch: |

Representing the total demand….. losses ,and whole PF  for the minimum load improvement

4.1.5   Optimum case :

In order to get the optimum case we take all improvements together, that suggestion for optimum case is increasing the voltage of swing bus up to (0.25%) and increasing the tap ratio up to (0.05%) and adding the capacitors  as shown

The results of this case can be shown in the following table :

| AMP | %PF | MVA | Mvar | MW | Bus total load (kv) | Bus |
| --- | --- | --- | --- | --- | --- | --- |
| 642.28 | 91.6 | 0.438 | 0.176 | 0.402 | 0.400 | Bus14 |
| 407.82 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus15 |
| 413.03 | 90.8 | 0.276 | 0.116 | 0.251 | 0.400 | Bus21 |
| 642.44 | 90.5 | 0.438 | 0.186 | 0.397 | 0.400 | Bus26 |
| 467.44 | 90.3 | 0.318 | 0.137 | 0.287 | 0.400 | Bus27 |
| 734.46 | 92.4 | 0.502 | 0.192 | 0.464 | 0.400 | Bus28 |
| 501.95 | 86.2 | 0.345 | 0.175 | 0.297 | 0.400 | Bus39 |
| 258.26 | 91.3 | 0.173 | 0.070 | 0.158 | 0.400 | Bus47 |
| 408.14 | 92.0 | 0.278 | 0.109 | 0.256 | 0.400 | Bus52 |
| 651.46 | 91.4 | 0.435 | 0.176 | 0.397 | 0.400 | Bus59 |
| 408.45 | 90.4 | 0.278 | 0.119 | 0.251 | 0.400 | Bus62 |
| 643.34 | 90.7 | 0.438 | 0.184 | 0.397 | 0.400 | Bus63 |
| 413.68 | 91.0 | 0.276 | 0.114 | 0.251 | 0.400 | Bus67 |
| 408.72 | 91.7 | 0.278 | 0.111 | 0.255 | 0.400 | Bus74 |
| 644.01 | 92.0 | 0.438 | 0.172 | 0.403 | 0.400 | Bus76 |
| 808.96 | 91.6 | 0.547 | 0.220 | 0.501 | 0.400 | Bus82 |
| 414.21 | 89.9 | 0.276 | 0.121 | 0.248 | 0.400 | Bus94 |
| 653.67 | 90.0 | 0.434 | 0.189 | 0.390 | 0.400 | Bus106 |
| 653.55 | 92.0 | 0.434 | 0.170 | 0.399 | 0.400 | Bus107 |
| 259.39 | 90.0 | 0.172 | 0.075 | 0.155 | 0.400 | Bus108 |
| 415.12 | 89.9 | 0.275 | 0.121 | 0.248 | 0.400 | Bus111 |
| 415.12 | 90.0 | 0.275 | 0.120 | 0.248 | 0.400 | Bus114 |
| 415.09 | 91.0 | 0.275 | 0.114 | 0.251 | 0.400 | Bus116 |
| 409.89 | 90.9 | 0.277 | 0.116 | 0.252 | 0.400 | Bus120 |
| 409.90 | 91.0 | 0.277 | 0.115 | 0.252 | 0.400 | Bus130 |
| 415.15 | 91.3 | 0.275 | 0.112 | 0.251 | 0.400 | Bus132 |
| 654.04 | 91.0 | 0.434 | 0.180 | 0.395 | 0.400 | Bus136 |
| 446.61 | 82.8 | 0.305 | 0.171 | 0.253 | 0.400 | Bus138 |
| 619.81 | 92.0 | 0.417 | 0.163 | 0.383 | 0.400 | Bus147 |
| 409.04 | 91.4 | 0.278 | 0.113 | 0.254 | 0.400 | Bus148 |
| 409.05 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus153 |
| 404.69 | 92.0 | 0.280 | 0.110 | 0.257 | 0.400 | Bus155 |
| 406.72 | 91.0 | 0.279 | 0.116 | 0.254 | 0.400 | Bus156 |
| 407.78 | 89.9 | 0.278 | 0.122 | 0.250 | 0.400 | Bus182 |
| 642.46 | 90.0 | 0.438 | 0.191 | 0.395 | 0.400 | Bus183 |
| 407.91 | 90.0 | 0.278 | 0.121 | 0.250 | 0.400 | Bus184 |
| 642.38 | 90.0 | 0.438 | 0.191 | 0.395 | 0.400 | Bus185 |
| 642.38 | 90.0 | 0.438 | 0.191 | 0.395 | 0.400 | Bus186 |
| 407.94 | 92.0 | 0.278 | 0.109 | 0.256 | 0.400 | Bus188 |
| 473.43 | 91.4 | 0.322 | 0.131 | 0.294 | 0.400 | Bus189 |
| 480.12 | 91.6 | 0.320 | 0.128 | 0.293 | 0.400 | Bus191 |
| 643.00 | 89.9 | 0.438 | 0.192 | 0.394 | 0.400 | Bus199 |
| 409.18 | 90.0 | 0.278 | 0.121 | 0.250 | 0.400 | Bus202 |
| 409.44 | 92.0 | 0.278 | 0.109 | 0.255 | 0.400 | Bus208 |
| 409.05 | 91.0 | 0.278 | 0.115 | 0.253 | 0.400 | Bus211 |
| 408.72 | 91.7 | 0.278 | 0.111 | 0.255 | 0.400 | Bus212 |

The busses information at optimum case

| %PF | MVA | Mvar | MW |  |
| --- | --- | --- | --- | --- |
| 92.05 lagging | 15.490 | 6.054 | 14.258 | Swing Bus(es): |
| 100.00 lagging | 0.000 | 0.000 | 0.000 | Generators: |
| 92.05 laggin | 15.490 | 6.054 | 14.258 | Total Demand: |
| 90.93 lagging | 12.438 | 5.176 | 11.310 | Total Motor Load: |
|  |  | 0.599 | 2.586 | Total Static Load: |
|  |  | 0.279 | 0.362 | Apparent Losses: |
|  |  | 0.000 | 0.000 | System Mismatch: |

Representing the total demand….. losses ,and whole PF  for the optimum case improvement.

CHAPTER FIVE

ECONOMECAL STUDY FOR IMPROVEMENT

Economical study

We must get these for our study

The old power is 90.65

The new power is 92

The penalties that will be achieved by improving the power factor =penalties before improvement –penalties after improvement (and this value =zero )

Penalties before improvement =.01*2*(total pill)

The total pill=.75*Pmax *876

=.75*14.237*120*.02*4000

=1025064$/yearly

And this value that will be saving after improvement

The initial cost for our improvement =.6*5000$=3000$

The S.P.B.P=investment/saving

=3000/102506.4

=0.02926

=.02926*365

=10.68 day