Chapter One :  Palestine Network

1.1  Electricity status in Palestine:

Due to the Israeli occupation Palestine has not yet a unified power system; the existing networks are local low voltage distribution networks.

The main supply for electrical distribution networks in the West Bank and Gaza is the Israeli Electrical Company (IEC).

The voltages of the existing distribution networks are 0.4, 6.6, 11, 22 , and 33 KV . IEC supplies electricity to the electrified communities by 22 or 33 KV by overhead lines . Electricity is purchased from IEC and then distributed to the consumers.

The results of the survey indicated that 99.6%of households in the Palestinian Territory were connected to the public electricity network in April 2008 , where this percentage was 99.3% during April 2006, and was 97.2% during July 2005, while it was 97.2% during the same month1999 .  0.3% have no electricity services, 0.1% of the households have their own generators.

From the results of the survey, it is noted that south of the West Bank has the lowest percentage of households connected to electricity network (99.0%). The situation is different in Gaza Strip which has 99.6% of the households connected to electricity network during April 2006.

1.2  Purchases of Electrical Energy

Due to the Palestinian Central Bureau of Statistics during 2008 , total electrical energy purchases in the Palestinian Territory reached 3,441,700 MWh; 2,331,110 MWh in the West Bank and 1,110,590 MWh in Gaza Strip(765,290 MWh imported from Israel and 345,300 MWh produced by Gaza Power Plant).

1.3 Household Consumption of electricity

The results of the survey indicated that the average household electricity consumption (from the households that used electricity) in the Palestinian Territory during April2008 was 282 KWh.

While during April2006 was 211 KWh, where this average was 380.1 KWh during July 2005, and it was 380.1KWh during the same month 1999. This average ranged by region and type of locality in April 2008, it reached 367 KWh in the Middle of the West Bank and didn’t exceed 217 KWh in the North of West Bank. This average was about 293 KWh in urban localities and 205 KWh in rural localities, and 357 KWh in refugee camps.

And the average per capita electricity consumption in the Palestinian Territory during April 2008 was 48.6 KWh.

While during April 2006 was 39.7 KWh.

1.4 Electrical Sources and Network

problems

There are many problems that the consumer face it in the network.

The level of electrical services provided by the IEC is inadequate, which constitutes a handicap for the industrial sector, high economic losses, and an obstacle for the development of the country. With an electricity consumption level of 583 kWh/person (1999), the lowest consumption level in the region , the Palestinian Territories barely manage to satisfy their electric needs, whereas in Israel electricity consumption exceeds 6000 kWh/person.

This gap can be mainly explained by an inadequate electricity

Infra structure, high transmission losses (25%) and high electricity prices.

Palestinian electricity consumption appears to be inelastic. However, the Palestinian electricity sector shows a high vulnerability to political shocks. The influence of conflict on

the electricity sector goes beyond direct destruction. It results in a modification of the

trajectory of electricity consumption, a deceleration in the growth rate, and the retardation of a “healthy” recovery.

Electricity problems and priorities can be summarized as follows:

The lack of investment and public expenditure, high prices, and high transmission losses constitute fundamental problems for the electricity sector. The quality of the electrical services is inadequate and below standard.

Another problem that the Israeli Electricity Corporation (IEC) imposes the municipalities and large consumer in Palestine to pay penalties if they cause a power factor less than 0.92 . The Jerusalem Electricity company (JEDCO) is the only company that imposes the three phase industrial consumers with PF penalties if their PF is less than 0.92 . On other hand , several municipalities in the West Bank and Gaza strip are in the process of imposing power factor penalties on industrial customers with low PF .

Table below show relation of PF to the penalties :

| PF | penalties |
| --- | --- |
| 0.92 or more | No penalties |
| Less than 0.92 to 0.8 | 1%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.8 to 0.7 | 1.25%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.7 | 1.5%of the total bill for every 0.01 of PF less than 0.92 |

1.5 Energy consumption in different sector    in Palestine

Electricity utilization is considered essential not only for the industrial and residential sectors, but also for water pumping and street lights. Data from the Palestinian Energy Authority for

electricity consumption indicates that the residential sector consumes (50 – 60)% of the total electricity against (12 – 14) % for the commercial sector and (10 – 12)% for industrial sector . Electricity consumption for both water pumping and street lights is 15% , (3 – 4)% respectively .

It can be shown as a table below:

| Type of sector | Percentage |
| --- | --- |
| Residential sector | (50 – 60)% |
| Industrial sector | (12 – 14) % |
| Commercial sector | (10 – 12)% |
| Water pumping | 15% |
| Street lighting | (3 – 4)% |

Chapter two : Jericho Network

2.1 Introduction to Jericho Network

Jericho electrical distribution network is fed from one connection point by the Jordan Electrical Company, at 33kv

The development of electrical energy purchased from JEC. and  growth rate are :

| Year | Annual Purchased M.W.H | Growth Rate % |
| --- | --- | --- |
| 2003 | 34727.4 | 0 |
| 2004 | 34727.4 | 0 |
| 2005 | 37273.8 | 7.3 |
| 2006 | 39264.8 | 5.34 |
| 2007 | 44708.0 | 13.86 |
| 2008 | 50830.96 | 13.7 |

The energy consumed is distributed into different types  :

| Type of load | Consumption |
| --- | --- |
| Residential | 45 % |
| Industrial | 25 % |
| HOTEL | 10 % |
| Military consumption | 20% |

The change of losses in the electrical distribution network as shown in the  table  :

| Year | ∆p % |
| --- | --- |
| 2004 | 12 % |
| 2005 | 9 % |
| 2007 | 7 % |
| 2008 | 6 % |

But in 2009 it decreases to reach about  5  %  for max case in summer .because using conditioning .

2.2 Elements Of The Network

1. Electrical Supply:

One connection point  with tow feeder  at 33 kV from AL_swaimah Station In Jordan.

The peak power consumption is 15 MW

2. Medium voltage lines (Transmission line) :

There are two type of conductor :

- The Over Head Lines :

The Over Head Lines used in the network are  33KV , 11KV ACSR (Aluminum conductor steel reinforced )

With three cross sectional areas ( 50mm2 , 95mm2and 120mm2 XLPE  called Rabbit)

- Under ground cables :

Under ground cables used in the network are

33KV ,11 KV    1*(3*120), 1*(3*150) ACSR

The resistance / km and reactance / km  and max current for all T.L ( Over head  lines and under ground cables ) as shown :

| Type of T.L | Resistance Ohms/Km | Reactance Ohms/Km | Max current capacity (A) |
| --- | --- | --- | --- |
| O.H.L Rabbit 50 mm2 | 0.543 | 0.333 | 174 |
| O.H.L Dog 95 mm2 | 0.301 | 0.332 | 250 |
| UGC Al 95 mm2 | 0.41 | 0.121 | 250 |
| UGC Cu 120 mm2 | 0.196 | 0.117 | 360 |
| UGC Cu 150 mm2 | 0.159 | 0.114 | 410 |

3. Distribution Transformers :

Number of distribution transformers in  Jericho  network are 87 transformer .

All transformer   33KV / 0.4KV and 11KV/0.4KV  Δ-Υ connected , distribution transformers with deferent  ratings as shown  in the table and the rating of this transformer 630 ,500 , 400 , 250 KVA

| Transformer Ratings KVA | No. of Transformers |
| --- | --- |
| 1000 | 3 |
| 630 | 13 |
| 500 | 11 |
| 400 | 18 |
| 160 | 19 |
| 100 | 22 |

2.3   Problems  in Jericho   network :

- the main T.L coming from the connection point is  Rabbit ( 120mm2  ) did not have the capability to hold the over current resulting in cutting off the supply on the maximum load condition , because total current pass from this line equal 344 A but max capacity current of this line is 174 A.

- Bad distribution of the loads on the existing Transformers which cause a poor load factor , because there are some transformers work at max load factor more than 100 % and some transformers work with load factor less than 60 % .

Note that the transformer work with max efficiency when load factor between ( 65-75 ) %.

Solution: change the configuration of some branches and transformers  .

- One connection point and this lead to make the performance of the  network  weak .

( no reliability in network  )

Solution: it is very important to get another connection point to supply the city .

- High drop voltage : this effect on the losses in the network and this drop voltage accurse in summer

- Solution: use capacitor banks ( fixed or variable )

Chapter three : Load Flow Analysis

3.1 Load flow study :

In power engineering, the power flow study (also known as load-flow study) is an important tool involving numerical analysis applied to a power system. Unlike traditional circuit analysis, a power flow study usually uses simplified notation such as a one-line diagram and per-unit system, and focuses on various forms of AC power (ie: reactive, real, and apparent) rather than voltage and current. It analyses the power systems in normal steady-state operation. There exist a number of software implementations of power flow studies.

In addition to a power flow study itself, sometimes called the base case, many software implementations perform other types of analysis, such as short-circuit fault analysis and economic analysis. In particular, some programs use linear programming to find the optimal power flow, the conditions which give the lowest cost per kilowatt generated.

The great importance of power flow or load-flow studies is in the planning the future expansion of power systems as well as in determining the best operation of existing systems. The principal information obtained from the power flow study is the magnitude and phase angle of the voltage at each bus and the real and reactive power flowing in each line.

In our project we use the ETAP software to analyze Jericho network .

3.2 ETAP Power Station Program:

With ETAP’s advanced Load Flow module, you can create and validate your system model with ease and obtain accurate and reliable results. Built-in features like automatic device evaluation, summary alarms / warnings, result analyzer, and intelligent graphics make it the most efficient Load Flow program available today.

ETAP calculates bus voltages, branch power factors, currents, and power flows throughout the electrical system. ETAP allows for swing, voltage regulated, and unregulated power sources with multiple power grids and generator connections. It is capable of performing analysis on both radial and loop systems. ETAP allows you to select from several different methods in order to achieve the best calculation efficiency and accuracy.

]

Features of ETAP:

- Newton-Raphson , fast decoupled, & accelerated 
Gauss Seidel

- Generator governors with isochronous or droop mode

- Generator exciters with AVR or Mvar / PF controllers

- Transformer load tap changers (LTC / regulators)

- Advanced solution techniques for fast convergence

- Multiple loading conditions

- Multiple generation conditions

- Swing, voltage regulated, & unregulated power sources

- Voltage drop calculations

- Load forecasting

- Alert view to display critical & marginal limit violations

- Bus / transformer / cable overload warning

- Single-phase load flow display

- Global & individual bus diversity factors

- Individual demand factors for continuous, intermittent, 
& spare operating conditions

- Option to update the initial condition from load flow solutions

- Phase-shifting transformer

- Power factor correction

- Multi-report result analyzer

- 10,000+ bus capability

3.3 In this semester we do the following steps:

Step1: collection of data which consist of :

- Actual loads on transformer and power factor .

- Impedances of transmission lines ( R, X) .

- Draw the line diagram from map

Step2: Plotting the one line diagram in ETAP .

Step 3: Analysis and study of the MAX. case

Table of transformers’ loading

| Transformer | S RATED KVA | S ACTUAL KVA | LF % |
| --- | --- | --- | --- |
| 1 | 250 | 210 | 84 |
| 2 | 160 | 110 | 68.75 |
| 3 | 250 | 225 | 90 |
| 4 | 400 | 360 | 90 |
| 5 | 100 | 90 | 90 |
| 6 | 100 | 85 | 85 |
| 7 | 500 | 420 | 84 |
| 8 | 250 | 210 | 84 |
| 9 | 250 | 210 | 84 |
| 10 | 400 | 360 | 90 |
| 11 | 250 | 220 | 88 |
| 12 | 500 | 430 | 86 |
| 13 | 500 | 490 | 98 |
| 14 | 630 | 550 | 87.3 |
| 15 | 250 | 223 | 89.2 |
| 16 | 160 | 154 | 96.25 |
| 17 | 100 | 93 | 93 |
| 18 | 100 | 90 | 90 |
| 19 | 100 | 88 | 88 |
| 20 | 630 | 560 | 88.8 |
| 21 | 400 | 370 | 92.5 |
| 22 | 160 | 154 | 96.25 |
| 23 | 250 | 230 | 92 |
| 24 | 100 | 87 | 87 |
| 25 | 160 | 133 | 83.12 |
| 26 | 160 | 140 | 87.5 |
| 27 | 160 | 143 | 89.37 |
| 28 | 630 | 540 | 85.7 |
| 29 | 250 | 230 | 92 |
| 30 | 500 | 460 | 92 |
| 31 | 400 | 370 | 92.5 |
| 32 | 250 | 244 | 97.6 |
| 33 | 100 | 76 | 76 |
| 34 | 250 | 188 | 75.2 |
| 35 | 250 | 190 | 76 |
| 36 | 400 | 350 | 87.5 |
| 37 | 160 | 120 | 75 |
| 38 | 100 | 76 | 76 |
| 39 | 630 | 532 | 84.4 |
| 40 | 100 | 93 | 93 |
| 41 | 630 | 522 | 82.8 |
| 42 | 250 | 210 | 84 |
| 43 | 160 | 142 | 88.75 |
| 44 | 250 | 189 | 75.6 |
| 45 | 100 | 92 | 92 |
| 46 | 400 | 362 | 90.5 |
| 47 | 100 | 75 | 75 |
| 48 | 250 | 210 | 84 |
| 49 | 250 | 202 | 80.8 |
| 50 | 630 | 600 | 95.2 |
| 51 | 630 | 580 | 92.06 |
| 52 | 100 | 92 | 92 |
| 53 | 250 | 220 | 88 |
| 54 | .400 | 350 | 87.5 |
| 55 | 400 | 360 | 90 |
| 56 | 400 | 380 | 95 |
| 57 | 400 | 320 | 80 |
| 58 | 400 | 380 | 95 |
| 59 | 400 | 320 | 80 |
| 60 | 400 | 360 | 90 |
| 61 | 630 | 530 | 84.12 |
| 62 | 400 | 330 | 82.5 |
| 63 | 250 | 210 | 84 |
| 64 | 100 | 92 | 92 |
| 65 | 160 | 120 | 75 |
| 66 | 100 | 82 | 82 |
| 67 | 250 | 208 | 83.2 |
| 68 | 100 | 93 | 93 |
| 69 | 160 | 109 | 68.125 |
| 70 | 250 | 210 | 84 |
| 71 | 250 | 208 | 83.2 |
| 72 | 250 | 240 | 96 |
| 73 | 100 | 77 | 77 |
| 74 | 630 | 507 | 80.4 |
| 75 | 500 | 410 | 82 |
| 76 | 250 | 203 | 81.2 |
| 77 | 250 | 188 | 75.2 |
| 78 | 250 | 172 | 68.8 |
| 79 | 400 | 320 | 80 |
| 80 | 400 | 350 | 87.5 |
| 81 | 250 | 208 | 83.2 |
| 82 | 400 | 280 | 70 |
| 83 | 250 | 192 | 76.8 |
| 84 | 1000 | 920 | 92 |
| 85 | 1000 | 880 | 88 |
| 86 | 1000 | 900 | 90 |
| 87 | 160 | 95 | 59.37 |

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):          11.273         9.415              14.687                     76.8  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         11.273         9.415              14.687                     76.8  Lagging

---------     ---------     ---------     --------------

Total Motor Load :                     3.779          2.342           4.446                       85.0  Lagging

Total Static Load:         6.655         3.026

Apparent Losses:            0.838         4.047

Total current  257 A .

From the result we can notice that :

- P = 11.273  MW  and  ∆p = 0.838 MW

Then ∆p % = 0.838 \ 11.273 =  5 %

There are problems in network as shown in the  Jericho :

network problems , such as the drop voltages in the network which effect on the P.F and on losses .

- Problem in load factor as shown in the above .

We put all result data on the appendix.

3.4  Future Study   :

- Improvement the max . case ( improve V, P.F, decrease losses )  by :

- Raise the swing bus about 5 % ( 33 KV to 34.65 KV ) .

- Using capacitor banks (fixed and variable ) .

- Study the min . case and fault case and  their       improvement.

- Tow  connection points :

- Without ring .

- With ring .

- Switch gear case .

- Economical study.

Chapter FOUR : Analysis of maximum case

Before improvement (original case)  4.1

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):          12.7         7.36              14.687                     86.8  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         12.7         7.36              14.687                     86.8  Lagging

---------     ---------     ---------     --------------

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.391 | 0.18 | 0.11 | 0.861 |
| 5 | 0.400 | 0.385 | 0.33 | 0.19 | 0.867 |
| 6 | 0.400 | 0.383 | 0.20 | 0.12 | 0.863 |
| 7 | 0.400 | 0.384 | 0.14 | 0.08 | 0.87 |
| 8 | 0.400 | 0.386 | 0.14 | 0.08 | 0.875 |
| 9 | 0.400 | 0.384 | 0.16 | 0.09 | 0.882 |
| 10 | 0.400 | 0.384 | 0.21 | 0.11 | 0.89 |
| 13 | 0.400 | 0.385 | 0.16 | 0.08 | 0.9 |
| 15 | 0.400 | 0.385 | 0.20 | 0.12 | 0.862 |
| 18 | 0.400 | 0.375 | 0.29 | 0.17 | 0.865 |
| 19 | 0.400 | 0.384 | 0.24 | 0.13 | 0.881 |
| 20 | 0.400 | 0.382 | 0.56 | 0.27 | 0.902 |
| 22 | 0.400 | 0.382 | 0.17 | 0.08 | 0.911 |
| 24 | 0.400 | 0.380 | 0.43 | 0.27 | 0.851 |
| 25 | 0.400 | 0.384 | 0.10 | 0.06 | 0.861 |
| 28 | 0.400 | 0.385 | 0.13 | 0.07 | 0.891 |
| 31 | 0.400 | 0.385 | 0.09 | 0.05 | 0.889 |
| 32 | 0.400 | 0.378 | 0.21 | 0.13 | 0.851 |
| 33 | 0.400 | 0.379 | 0.19 | 0.12 | 0.857 |
| 36 | 0.400 | 0.386 | 0.13 | 0.08 | 0.855 |
| 38 | 0.400 | 0.386 | 0.23 | 0.12 | 0.891 |
| 40 | 0.400 | 0.385 | 0.10 | 0.05 | 0.91 |
| 41 | 0.400 | 0.386 | 0.07 | 0.04 | 0.875 |
| 42 | 0.400 | 0.384 | 0.18 | 0.1 | 0.872 |
| 48 | 0.400 | 0.381 | 0.32 | 0.19 | 0.864 |
| 52 | 0.400 | 0.381 | 0.30 | 0.14 | 0.908 |
| 59 | 0.400 | 0.382 | 0.25 | 0.12 | 0.905 |
| 62 | 0.400 | 0.381 | 0.18 | 0.09 | 0.896 |
| 63 | 0.400 | 0.373 | 0.29 | 0.15 | 0.888 |
| 65 | 0.400 | 0.372 | 0.29 | 0.16 | 0.876 |
| 70 | 0.400 | 0.382 | 0.16 | 0.1 | 0.854 |
| 72 | 0.400 | 0.379 | 0.22 | 0.13 | 0.867 |
| 73 | 0.400 | 0.379 | 0.10 | 0.05 | 0.892 |
| 74 | 0.400 | 0.378 | 0.23 | 0.1 | 0.916 |
| 81 | 0.400 | 0.379 | 0.20 | 0.09 | 0.912 |
| 82 | 0.400 | 0.381 | 0.12 | 0.06 | 0.899 |
| 83 | 0.400 | 0.379 | 0.19 | 0.09 | 0.905 |
| 85 | 0.400 | 0.377 | 0.17 | 0.1 | 0.861 |
| 92 | 0.400 | 0.379 | 0.13 | 0.08 | 0.861 |
| 95 | 0.400 | 0.380 | 0.12 | 0.07 | 0.866 |
| 96 | 0.400 | 0.380 | 0.20 | 0.11 | 0.875 |
| 101 | 0.400 | 0.381 | 0.20 | 0.12 | 0.862 |
| 105 | 0.400 | 0.380 | 0.16 | 0.09 | 0.874 |
| 108 | 0.400 | 0.382 | 0.29 | 0.15 | 0.891 |
| 110 | 0.400 | 0.379 | 0.18 | 0.11 | 0.854 |

Raise the swing voltage from 33 kV to 34.65kV 4.2

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):          14.6        8.415             16.87                     86.7 Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:        14.6        8.415              16.87                     86.7 Lagging

---------     ---------     ---------     -----------

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.412 | 4.9 | 0.12 | 0.861 |
| 5 | 0.400 | 0.406 | 2.73 | 0.21 | 0.867 |
| 6 | 0.400 | 0.403 | 4.5 | 0.13 | 0.863 |
| 7 | 0.400 | 0.408 | 6.29 | 0.09 | 0.87 |
| 8 | 0.400 | 0.405 | 6.14 | 0.09 | 0.875 |
| 9 | 0.400 | 0.405 | 5.34 | 0.10 | 0.882 |
| 10 | 0.400 | 0.407 | 4.26 | 0.12 | 0.89 |
| 13 | 0.400 | 0.405 | 5.38 | 0.09 | 0.9 |
| 15 | 0.400 | 0.406 | 4.52 | 0.13 | 0.862 |
| 18 | 0.400 | 0.395 | 3.22 | 0.18 | 0.865 |
| 19 | 0.400 | 0.405 | 3.83 | 0.14 | 0.881 |
| 20 | 0.400 | 0.403 | 1.59 | 0.30 | 0.902 |
| 22 | 0.400 | 0.403 | 5.02 | 0.09 | 0.911 |
| 24 | 0.400 | 0.401 | 2.20 | 0.28 | 0.851 |
| 25 | 0.400 | 0.405 | 6.56 | 0.09 | 0.861 |
| 28 | 0.400 | 0.399 | 6.36 | 0.08 | 0.891 |
| 31 | 0.400 | 0.405 | 10.3 | 0.05 | 0.889 |
| 32 | 0.400 | 0.398 | 4.40 | 0.14 | 0.851 |
| 33 | 0.400 | 0.399 | 4.62 | 0.13 | 0.857 |
| 36 | 0.400 | 0.407 | 6.73 | 0.09 | 0.855 |
| 38 | 0.400 | 0.404 | 3.63 | 0.14 | 0.891 |
| 40 | 0.400 | 0.406 | 7.59 | 0.06 | 0.91 |
| 41 | 0.400 | 0.407 | 11.06 | 0.05 | 0.875 |
| 42 | 0.400 | 0.405 | 5.10 | 0.11 | 0.872 |
| 48 | 0.400 | 0.402 | 2.77 | 0.21 | 0.864 |
| 52 | 0.400 | 0.402 | 2.88 | 0.16 | 0.908 |
| 59 | 0.400 | 0.403 | 3.35 | 0.14 | 0.905 |
| 62 | 0.400 | 0.402 | 5.50 | 0.09 | 0.896 |
| 63 | 0.400 | 0.394 | 3.04 | 0.17 | 0.888 |
| 65 | 0.400 | 0.392 | 3.23 | 0.17 | 0.876 |
| 70 | 0.400 | 0.403 | 5.53 | 0.11 | 0.854 |
| 72 | 0.400 | 0.400 | 4.10 | 0.14 | 0.867 |
| 73 | 0.400 | 0.400 | 8.44 | 0.06 | 0.892 |
| 74 | 0.400 | 0.399 | 3.98 | 0.11 | 0.916 |
| 81 | 0.400 | 0.400 | 4.49 | 0.10 | 0.912 |
| 82 | 0.400 | 0.402 | 6.95 | 0.07 | 0.899 |
| 83 | 0.400 | 0.400 | 4.70 | 0.10 | 0.905 |
| 85 | 0.400 | 0.398 | 5.37 | 0.11 | 0.861 |
| 92 | 0.400 | 0.400 | 6.56 | 0.09 | 0.861 |
| 95 | 0.400 | 0.400 | 7.21 | 0.08 | 0.866 |
| 96 | 0.400 | 0.401 | 4.61 | 0.12 | 0.875 |
| 101 | 0.400 | 0.402 | 4.20 | 0.14 | 0.862 |
| 105 | 0.400 | 0.400 | 5.55 | 0.10 | 0.874 |
| 108 | 0.400 | 0.403 | 3.18 | 0.16 | 0.891 |
| 110 | 0.400 | 0.399 | 5.07 | 0.12 | 0.854 |

Chapter FIVE:

POWER FACTOR IMPROVEMENT

As the Power Distribution network must be dimensioned to carry the apparent current, the optimum apparent current shall be maintained by improving the Power Factor close to unity. If appropriately sized capacitor banks or automatic systems are installed in parallel to the loads, the Reactive Current circulates between the capacitor and the load. This effectively means rest of the distribution network or the source is not subject to this additional Reactive Power. If Power Factor of unity is achieved by suitable combination of systems, the main current in the distribution is Active Power only .

Reactive Current circulating between the source and the load converts the electrical energy into heat. There is an additional load on the transformer, cables, switchgear etc., through the I2RT losses. This energy losses and voltage drops leads to additional loading on the source. If higher proportion of Reactive current is present, such losses will be higher and the distribution network shall have to be over sized to transmit Useful Power ‘P’ .

Effect of Low Power Factor

1. Higher Apparent Current.

Low Power Factor causes higher Apparent Current in any Load Centre.

2. Higher Losses in the Electrical Distribution System.

The loss in the Cables, Switches, Motors etc., are in square proportion of the Active Current leading to higher losses in the Electrical Systems. The higher Active Current passing through all electrical circuits, cables, bus bars, switches, motors etc., reduces the life of the components.

The electrical losses at a higher level will lead to higher resistive loss in square proportion of the Active Current, in turn leading to higher monthly consumption bills.

3.Low Voltage in the System.

The low power factor leads to low voltage which leads to motor winding burn-outs.

4. Low Plant Load Factor.

The low power factor reduces the capacity of the distribution network.

Low Power Factor increases the maintenance cost of the Power Distribution System.

Benefits of Improving Power Factor :

- Lower Apparent Power.

- Reduced KWH Losses.

- Improved Voltage leading to enhanced life of the transformer, cables, switchgear, motors etc., and lower energy cost.

Power factor correction by means of conventional capacitor banks will not be effective where the level of harmonics are higher. This is because the harmonic-currents are amplified in the parallel resonant circuit formed by the capacitor and the network. As a result, current and voltage distortion are further increased.

The first step is to raise the power factor to be 92% to avoid penalties .so we’ll add capacitors to meet this value of power factor.

Power factor improvement

PF old = 86.8 %

PF desired = 92%

We can obtain QC needed by the equation

Q c = Q old – Q new =P [tan cos-1(PF old) - tan cos-1(0.92)]

We’ll get Qc =1.8 MVAr

Adding capacitors in delta connection parallel to the Transformer in secondary side (0.4 kV) .

POWER FACTOR IMPROVEMENT SUMMARY

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):          12.7         5.56              13.863                     92  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         12.7         5.56              13.863                     92  Lagging

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.391 | 0.18 | 0.084 | 0.912 |
| 5 | 0.400 | 0.385 | 0.33 | 0.14 | 0.921 |
| 6 | 0.400 | 0.383 | 0.20 | 0.092 | 0.912 |
| 7 | 0.400 | 0.384 | 0.14 | 0.076 | 0.88 |
| 8 | 0.400 | 0.386 | 0.14 | 0.08 | 0.875 |
| 9 | 0.400 | 0.384 | 0.16 | 0.09 | 0.882 |
| 10 | 0.400 | 0.384 | 0.21 | 0.11 | 0.89 |
| 13 | 0.400 | 0.385 | 0.16 | 0.08 | 0.9 |
| 15 | 0.400 | 0.385 | 0.20 | 0.09 | 0.915 |
| 18 | 0.400 | 0.375 | 0.29 | 0.14 | 0.902 |
| 19 | 0.400 | 0.384 | 0.24 | 0.125 | 0.889 |
| 20 | 0.400 | 0.382 | 0.56 | 0.27 | 0.902 |
| 22 | 0.400 | 0.382 | 0.17 | 0.075 | 0.921 |
| 24 | 0.400 | 0.380 | 0.43 | 0.195 | 0.913 |
| 25 | 0.400 | 0.384 | 0.10 | 0.045 | 0.913 |
| 28 | 0.400 | 0.385 | 0.13 | 0.067 | 0.898 |
| 31 | 0.400 | 0.385 | 0.09 | 0.05 | 0.889 |
| 32 | 0.400 | 0.378 | 0.21 | 0.101 | 0.901 |
| 33 | 0.400 | 0.379 | 0.20 | 0.084 | 0.921 |
| 36 | 0.400 | 0.386 | 0.13 | 0.05 | 0.935 |
| 38 | 0.400 | 0.386 | 0.23 | 0.111 | 0.904 |
| 40 | 0.400 | 0.385 | 0.11 | 0.05 | 0.91 |
| 41 | 0.400 | 0.386 | 0.07 | 0.04 | 0.875 |
| 42 | 0.400 | 0.384 | 0.18 | 0.096 | 0.88 |
| 48 | 0.400 | 0.381 | 0.32 | 0.147 | 0.912 |
| 52 | 0.400 | 0.381 | 0.30 | 0.14 | 0.908 |
| 59 | 0.400 | 0.382 | 0.25 | 0.12 | 0.905 |
| 62 | 0.400 | 0.381 | 0.18 | 0.09 | 0.896 |
| 63 | 0.400 | 0.373 | 0.29 | 0.15 | 0.888 |
| 65 | 0.400 | 0.372 | 0.29 | 0.136 | 0.906 |
| 70 | 0.400 | 0.382 | 0.16 | 0.074 | 0.912 |
| 72 | 0.400 | 0.379 | 0.22 | 0.089 | 0.931 |
| 73 | 0.400 | 0.379 | 0.09 | 0.048 | 0.90 |
| 74 | 0.400 | 0.378 | 0.22 | 0.1 | 0.916 |
| 81 | 0.400 | 0.379 | 0.20 | 0.09 | 0.912 |
| 82 | 0.400 | 0.381 | 0.12 | 0.06 | 0.899 |
| 83 | 0.400 | 0.379 | 0.19 | 0.084 | 0.915 |
| 85 | 0.400 | 0.377 | 0.16 | 0.072 | 0.921 |
| 92 | 0.400 | 0.379 | 0.13 | 0.053 | 0.931 |
| 95 | 0.400 | 0.380 | 0.12 | 0.049 | 0.926 |
| 96 | 0.400 | 0.380 | 0.20 | 0.105 | 0.885 |
| 101 | 0.400 | 0.381 | 0.20 | 0.073 | 0.942 |
| 105 | 0.400 | 0.380 | 0.16 | 0.086 | 0.884 |
| 108 | 0.400 | 0.382 | 0.29 | 0.15 | 0.891 |
| 110 | 0.400 | 0.379 | 0.18 | 0.075 | 0.924 |

We note:

when we increase power factor the losses in the network decrease  .

Losses before p.f improvement = 0.808 Mw .

Losses  after p.f improvement = 0.790 Mw .

Comparison between the original case and the case of power factor improvement

| Bus # | Voltage before | Voltage after | P.f Before | p.f after |
| --- | --- | --- | --- | --- |
| 2 | 0.391 | 0.391 | 0.861 | 0.912 |
| 5 | 0.385 | 0.385 | 0.867 | 0.921 |
| 6 | 0.383 | 0.383 | 0.863 | 0.912 |
| 7 | 0.384 | 0.387 | 0.87 | 0.88 |
| 8 | 0.386 | 0.384 | 0.875 | 0.875 |
| 9 | 0.384 | 0.384 | 0.882 | 0.882 |
| 10 | 0.384 | 0.386 | 0.89 | 0.89 |
| 13 | 0.385 | 0.384 | 0.9 | 0.9 |
| 15 | 0.385 | 0.385 | 0.862 | 0.915 |
| 18 | 0.375 | 0.375 | 0.865 | 0.902 |
| 19 | 0.384 | 0.384 | 0.881 | 0.889 |
| 20 | 0.382 | 0.382 | 0.902 | 0.902 |
| 22 | 0.382 | 0.383 | 0.911 | 0.921 |
| 24 | 0.380 | 0.380 | 0.851 | 0.913 |
| 25 | 0.384 | 0.384 | 0.861 | 0.913 |
| 28 | 0.385 | 0.379 | 0.891 | 0.898 |
| 31 | 0.385 | 0.385 | 0.889 | 0.889 |
| 32 | 0.378 | 0.384 | 0.851 | 0.901 |
| 33 | 0.379 | 0.385 | 0.857 | 0.921 |
| 36 | 0.386 | 0.386 | 0.855 | 0.935 |
| 38 | 0.386 | 0.383 | 0.891 | 0.904 |
| 40 | 0.385 | 0.386 | 0.91 | 0.91 |
| 41 | 0.386 | 0.386 | 0.875 | 0.875 |
| 42 | 0.384 | 0.385 | 0.872 | 0.88 |
| 48 | 0.381 | 0.382 | 0.864 | 0.912 |
| 52 | 0.381 | 0.381 | 0.908 | 0.908 |
| 59 | 0.382 | 0.382 | 0.905 | 0.905 |
| 62 | 0.381 | 0.381 | 0.896 | 0.896 |
| 63 | 0.373 | 0.374 | 0.888 | 0.888 |
| 65 | 0.372 | 0.378 | 0.876 | 0.906 |
| 70 | 0.382 | 0.382 | 0.854 | 0.912 |
| 72 | 0.379 | 0.384 | 0.867 | 0.931 |
| 73 | 0.379 | 0.380 | 0.892 | 0.90 |
| 74 | 0.378 | 0.382 | 0.916 | 0.916 |
| 81 | 0.379 | 0.382 | 0.912 | 0.912 |
| 82 | 0.381 | 0.382 | 0.899 | 0.899 |
| 83 | 0.379 | 0.382 | 0.905 | 0.915 |
| 85 | 0.377 | 0.381 | 0.861 | 0.921 |
| 92 | 0.379 | 0.382 | 0.861 | 0.931 |
| 95 | 0.380 | 0.380 | 0.866 | 0.926 |
| 96 | 0.380 | 0.383 | 0.875 | 0.885 |
| 101 | 0.381 | 0.382 | 0.862 | 0.942 |
| 105 | 0.380 | 0.380 | 0.874 | 0.884 |
| 108 | 0.382 | 0.382 | 0.891 | 0.891 |
| 110 | 0.379 | 0.383 | 0.854 | 0.924 |

Chapter SIX:

THE IMPROVEMENT OF VOLTAGE LEVEL

Maximum load voltage level improvement :

Adding capacitors (fixed and regulated) in delta connection parallel to the Transformer in secondary side (0.4 kv)

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW               Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):             12.7               3.451        13.16                         96.5 Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         12. 7                7.36              14.687                  86.8  Lagging

---------     ---------     ---------     --------------

We notice

when we improvement the voltage level the losses in the network decrease and the total current decrease

Losses in origin case   = 0.808 Mw

Losses after voltage improvement = 0.635 Mw

Comparison between three  case

1.      the origin case .

2.      power factor improvement  case .

3.     voltage level improvement  case .

| Bus # | Voltage Origin case | Voltage Improve p.f | Voltage Improve of voltage level | P.f origin | p.f improve p.f | p.f Improve of voltage level |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | 0.391 | 0.391 | 0.395 | 0.861 | 0.912 | 99.80 |
| 5 | 0.385 | 0.385 | 0.389 | 0.867 | 0.921 | 97.43 |
| 6 | 0.383 | 0.383 | 0.389 | 0.863 | 0.912 | 99.45 |
| 7 | 0.384 | 0.387 | 0.390 | 0.87 | 0.88 | 97.15 |
| 8 | 0.386 | 0.384 | 0.387 | 0.875 | 0.875 | 97.17 |
| 9 | 0.384 | 0.384 | 0.387 | 0.882 | 0.882 | 97.04 |
| 10 | 0.384 | 0.386 | 0.390 | 0.89 | 0.89 | 99.77 |
| 13 | 0.385 | 0.384 | 0.387 | 0.9 | 0.9 | 97.23 |
| 15 | 0.385 | 0.385 | 0.388 | 0.862 | 0.915 | 97.07 |
| 18 | 0.375 | 0.375 | 0.381 | 0.865 | 0.902 | 97.76 |
| 19 | 0.384 | 0.384 | 0.387 | 0.881 | 0.889 | 96.46 |
| 20 | 0.382 | 0.382 | 0.385 | 0.902 | 0.902 | 96.47 |
| 22 | 0.382 | 0.383 | 0.387 | 0.911 | 0.921 | 98.90 |
| 24 | 0.380 | 0.380 | 0.386 | 0.851 | 0.913 | 99.01 |
| 25 | 0.384 | 0.384 | 0.387 | 0.861 | 0.913 | 98.42 |
| 28 | 0.385 | 0.379 | 0.383 | 0.891 | 0.898 | 97.70 |
| 31 | 0.385 | 0.385 | 0.385 | 0.889 | 0.889 | 94.10 |
| 32 | 0.378 | 0.384 | 0.385 | 0.851 | 0.901 | 98.81 |
| 33 | 0.379 | 0.385 | 0.386 | 0.857 | 0.921 | 99.42 |
| 36 | 0.386 | 0.386 | 0.387 | 0.855 | 0.935 | 92.60 |
| 38 | 0.386 | 0.383 | 0.385 | 0.891 | 0.904 | 95.58 |
| 40 | 0.385 | 0.386 | 0.386 | 0.91 | 0.91 | 93.30 |
| 41 | 0.386 | 0.386 | 0.387 | 0.875 | 0.875 | 94.70 |
| 42 | 0.384 | 0.385 | 0.385 | 0.872 | 0.88 | 93.00 |
| 48 | 0.381 | 0.382 | 0.384 | 0.864 | 0.912 | 95.83 |
| 52 | 0.381 | 0.381 | 0.384 | 0.908 | 0.908 | 95.53 |
| 59 | 0.382 | 0.382 | 0.387 | 0.905 | 0.905 | 99.46 |
| 62 | 0.381 | 0.381 | 0.386 | 0.896 | 0.896 | 98.85 |
| 63 | 0.373 | 0.374 | 0.380 | 0.888 | 0.888 | 98.32 |
| 65 | 0.372 | 0.378 | 0.379 | 0.876 | 0.906 | 98.10 |
| 70 | 0.382 | 0.382 | 0.385 | 0.854 | 0.912 | 98.15 |
| 72 | 0.379 | 0.384 | 0.384 | 0.867 | 0.931 | 99.40 |
| 73 | 0.379 | 0.380 | 0.386 | 0.892 | 0.90 | 99.40 |
| 74 | 0.378 | 0.382 | 0.383 | 0.916 | 0.916 | 97.15 |
| 81 | 0.379 | 0.382 | 0.383 | 0.912 | 0.912 | 96.65 |
| 82 | 0.381 | 0.382 | 0.384 | 0.899 | 0.899 | 96.92 |
| 83 | 0.379 | 0.382 | 0.383 | 0.905 | 0.915 | 96.61 |
| 85 | 0.377 | 0.381 | 0.381 | 0.861 | 0.921 | 96.82 |
| 92 | 0.379 | 0.382 | 0.383 | 0.861 | 0.931 | 96.43 |
| 95 | 0.380 | 0.380 | 0.383 | 0.866 | 0.926 | 97.80 |
| 96 | 0.380 | 0.383 | 0.384 | 0.875 | 0.885 | 96.99 |
| 101 | 0.381 | 0.382 | 0.386 | 0.862 | 0.942 | 99.49 |
| 105 | 0.380 | 0.380 | 0.384 | 0.874 | 0.884 | 98.81 |
| 108 | 0.382 | 0.382 | 0.384 | 0.891 | 0.891 | 95.66 |
| 110 | 0.379 | 0.383 | 0.383 | 0.854 | 0.924 | 97.29 |

Two connection points without ring configuration.

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):              7.8                4.4                     8.95                           87.1 Lagging

Generators:                5.000              3.000                5.8                               86.2Lagging

Total Demand:         12.8               7.4               14.75                             86.7  Lagging

I swing              :                156 A

I gen                 :                101 A

| Bus # | Voltage nom | Voltage Act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.392 | 0.19 | 0.11 | 0.861 |
| 5 | 0.400 | 0.386 | 0.33 | 0.19 | 0.867 |
| 6 | 0.400 | 0.385 | 0.20 | 0.12 | 0.863 |
| 7 | 0.400 | 0.390 | 0.14 | 0.08 | 0.87 |
| 8 | 0.400 | 0.387 | 0.14 | 0.08 | 0.875 |
| 9 | 0.400 | 0.387 | 0.17 | 0.09 | 0.882 |
| 10 | 0.400 | 0.389 | 0.21 | 0.11 | 0.89 |
| 13 | 0.400 | 0.387 | 0.165 | 0.08 | 0.9 |
| 15 | 0.400 | 0.388 | 0.20 | 0.12 | 0.862 |
| 18 | 0.400 | 0.378 | 0.29 | 0.17 | 0.865 |
| 19 | 0.400 | 0.387 | 0.242 | 0.13 | 0.881 |
| 20 | 0.400 | 0.385 | 0.564 | 0.27 | 0.902 |
| 22 | 0.400 | 0.385 | 0.176 | 0.08 | 0.911 |
| 24 | 0.400 | 0.383 | 0.43 | 0.27 | 0.851 |
| 25 | 0.400 | 0.387 | 0.101 | 0.06 | 0.861 |
| 28 | 0.400 | 0.381 | 0.137 | 0.07 | 0.891 |
| 31 | 0.400 | 0.388 | 0.097 | 0.05 | 0.889 |
| 32 | 0.400 | 0.381 | 0.217 | 0.13 | 0.851 |
| 33 | 0.400 | 0.382 | 0.199 | 0.12 | 0.857 |
| 36 | 0.400 | 0.390 | 0.131 | 0.08 | 0.855 |
| 38 | 0.400 | 0.387 | 0.23 | 0.12 | 0.891 |
| 40 | 0.400 | 0.389 | 0.109 | 0.05 | 0.91 |
| 41 | 0.400 | 0.390 | 0.07 | 0.04 | 0.875 |
| 42 | 0.400 | 0.388 | 0.179 | 0.1 | 0.872 |
| 48 | 0.400 | 0.385 | 0.32 | 0.19 | 0.864 |
| 52 | 0.400 | 0.386 | 0.303 | 0.14 | 0.908 |
| 59 | 0.400 | 0.387 | 0.255 | 0.12 | 0.905 |
| 62 | 0.400 | 0.386 | 0.18 | 0.09 | 0.896 |
| 63 | 0.400 | 0.378 | 0.289 | 0.15 | 0.888 |
| 65 | 0.400 | 0.377 | 0.29 | 0.16 | 0.876 |
| 70 | 0.400 | 0.387 | 0.164 | 0.1 | 0.854 |
| 72 | 0.400 | 0.385 | 0.22 | 0.13 | 0.867 |
| 73 | 0.400 | 0.385 | 0.09 | 0.05 | 0.892 |
| 74 | 0.400 | 0.383 | 0.22 | 0.1 | 0.916 |
| 81 | 0.400 | 0.385 | 0.20 | 0.09 | 0.912 |
| 82 | 0.400 | 0.387 | 0.12 | 0.06 | 0.899 |
| 83 | 0.400 | 0.384 | 0.19 | 0.09 | 0.905 |
| 85 | 0.400 | 0.382 | 0.17 | 0.1 | 0.861 |
| 92 | 0.400 | 0.384 | 0.13 | 0.08 | 0.861 |
| 95 | 0.400 | 0.385 | 0.12 | 0.07 | 0.866 |
| 96 | 0.400 | 0.386 | 0.19 | 0.11 | 0.875 |
| 101 | 0.400 | 0.387 | 0.20 | 0.12 | 0.862 |
| 105 | 0.400 | 0.386 | 0.16 | 0.09 | 0.874 |
| 108 | 0.400 | 0.389 | 0.29 | 0.15 | 0.891 |
| 110 | 0.400 | 0.388 | 0.18 | 0.11 | 0.854 |

Chapter SEVEN :

MINIMUM LOAD

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW               Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):             5.125                  2.862               5.87                   87.3  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         5.125                 2.862              5.87                   87.3  Lagging

---------     ---------     ---------     --------------

Total current  102.7 A .

| Bus # | Voltage nom | Voltage Act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.396 | 0.106 | 0.048 | 0.871 |
| 5 | 0.400 | 0.394 | 0.173 | 0.097 | 0.873 |
| 6 | 0.400 | 0.393 | 0.111 | 0.061 | 0.876 |
| 7 | 0.400 | 0.395 | 0.078 | 0.042 | 0.88 |
| 8 | 0.400 | 0.394 | 0.077 | 0.041 | 0.885 |
| 9 | 0.400 | 0.393 | 0.085 | 0.044 | 0.887 |
| 10 | 0.400 | 0.394 | 0.098 | 0.049 | 0.893 |
| 13 | 0.400 | 0.394 | 0.080 | 0.036 | 0.91 |
| 15 | 0.400 | 0.394 | 0.110 | 0.062 | 0.872 |
| 18 | 0.400 | 0.390 | 0.156 | 0.088 | 0.871 |
| 19 | 0.400 | 0.393 | 0.112 | 0.059 | 0.886 |
| 20 | 0.400 | 0.393 | 0.274 | 0.13 | 0.903 |
| 22 | 0.400 | 0.393 | 0.074 | 0.033 | 0.913 |
| 24 | 0.400 | 0.392 | 0.225 | 0.134 | 0.86 |
| 25 | 0.400 | 0.393 | 0.054 | 0.031 | 0.864 |
| 28 | 0.400 | 0.391 | 0.068 | 0.034 | 0.893 |
| 31 | 0.400 | 0.394 | 0.058 | 0.031 | 0.88 |
| 32 | 0.400 | 0.391 | 0.099 | 0.059 | 0.858 |
| 33 | 0.400 | 0.391 | 0.125 | 0.075 | 0.859 |
| 36 | 0.400 | 0.394 | 0.086 | 0.052 | 0.857 |
| 38 | 0.400 | 0.393 | 0.121 | 0.061 | 0.893 |
| 40 | 0.400 | 0.394 | 0.056 | 0.025 | 0.911 |
| 41 | 0.400 | 0.394 | 0.052 | 0.028 | 0.878 |
| 42 | 0.400 | 0.394 | 0.104 | 0.057 | 0.876 |
| 48 | 0.400 | 0.392 | 0.189 | 0.109 | 0.867 |
| 52 | 0.400 | 0.392 | 0.143 | 0.065 | 0.91 |
| 59 | 0.400 | 0.393 | 0.125 | 0.057 | 0.909 |
| 62 | 0.400 | 0.392 | 0.085 | 0.042 | 0.897 |
| 63 | 0.400 | 0.389 | 0.145 | 0.075 | 0.889 |
| 65 | 0.400 | 0.389 | 0.154 | 0.084 | 0.878 |
| 70 | 0.400 | 0.393 | 0.092 | 0.055 | 0.857 |
| 72 | 0.400 | 0.392 | 0.146 | 0.083 | 0.869 |
| 73 | 0.400 | 0.392 | 0.058 | 0.028 | 0.898 |
| 74 | 0.400 | 0.391 | 0.085 | 0.037 | 0.917 |
| 81 | 0.400 | 0.392 | 0.079 | 0.035 | 0.913 |
| 82 | 0.400 | 0.392 | 0.065 | 0.032 | 0.895 |
| 83 | 0.400 | 0.391 | 0.080 | 0.037 | 0.907 |
| 85 | 0.400 | 0.391 | 0.102 | 0.059 | 0.867 |
| 92 | 0.400 | 0.391 | 0.073 | 0.042 | 0.869 |
| 95 | 0.400 | 0.392 | 0.074 | 0.042 | 0.872 |
| 96 | 0.400 | 0.392 | 0.093 | 0.051 | 0.875 |
| 101 | 0.400 | 0.392 | 0.133 | 0.076 | 0.867 |
| 105 | 0.400 | 0.392 | 0.101 | 0.056 | 0.875 |
| 108 | 0.400 | 0.393 | 0.152 | 0.077 | 0.893 |
| 110 | 0.400 | 0.391 | 0.094 | 0.057 | 0.857 |

VOLTAGE LEVEL IMPROVEMENT  of   MINIMUM LOAD

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):             5.120               2.30                  5.67               91.4  Lagging

Generators:                0.000               0.000                0.000                  100.0  Lagging

Total Demand:         5.120              2.30                  5.67                91.4  Lagging

---------     ---------     ---------     --------------

Total current  99.2 A

Comparison between the case minimum load and voltage Level improvement of minimum load

| Bus # | Voltage before | Voltage after | P.f before | p.f after |
| --- | --- | --- | --- | --- |
| 2 | 0.396 | 0.398 | 0.871 | 91.8 |
| 5 | 0.394 | 0.396 | 0.873 | 92.4 |
| 6 | 0.393 | 0.395 | 0.876 | 89.7 |
| 7 | 0.395 | 0.394 | 0.88 | 92.8 |
| 8 | 0.394 | 0.395 | 0.885 | 88.8 |
| 9 | 0.393 | 0.396 | 0.887 | 90.8 |
| 10 | 0.394 | 0.394 | 0.893 | 91.7 |
| 13 | 0.394 | 0.394 | 0.91 | 91.9 |
| 15 | 0.394 | 0.392 | 0.872 | 90.8 |
| 18 | 0.390 | 0.394 | 0.871 | 89.4 |
| 19 | 0.393 | 0.394 | 0.886 | 89.2 |
| 20 | 0.393 | 0.393 | 0.903 | 90.8 |
| 22 | 0.393 | 0.393 | 0.913 | 91.5 |
| 24 | 0.392 | 0.394 | 0.86 | 89.7 |
| 25 | 0.393 | 0.393 | 0.864 | 88.3 |
| 28 | 0.391 | 0.394 | 0.893 | 90.2 |
| 31 | 0.394 | 0.394 | 0.88 | 88.3 |
| 32 | 0.391 | 0.393 | 0.858 | 87.4 |
| 33 | 0.391 | 0.394 | 0.859 | 88.3 |
| 36 | 0.394 | 0.394 | 0.857 | 89.6 |
| 38 | 0.393 | 0.394 | 0.893 | 90.3 |
| 40 | 0.394 | 0.395 | 0.911 | 91.2 |
| 41 | 0.394 | 0.394 | 0.878 | 89.1 |
| 42 | 0.394 | 0.393 | 0.876 | 89.8 |
| 48 | 0.392 | 0.393 | 0.867 | 88.5 |
| 52 | 0.392 | 0.393 | 0.91 | 92.4 |
| 59 | 0.393 | 0.394 | 0.909 | 92.6 |
| 62 | 0.392 | 0.392 | 0.897 | 91.3 |
| 63 | 0.389 | 0.391 | 0.889 | 90.1 |
| 65 | 0.389 | 0.393 | 0.878 | 91.3 |
| 70 | 0.393 | 0.392 | 0.857 | 89.7 |
| 72 | 0.392 | 0.392 | 0.869 | 88.7 |
| 73 | 0.392 | 0.393 | 0.898 | 91.4 |
| 74 | 0.391 | 0.392 | 0.917 | 92.9 |
| 81 | 0.392 | 0.393 | 0.913 | 92.8 |
| 82 | 0.392 | 0.392 | 0.895 | 90.4 |
| 83 | 0.391 | 0.392 | 0.907 | 90.8 |
| 85 | 0.391 | 0.392 | 0.867 | 89.3 |
| 92 | 0.391 | 0.392 | 0.869 | 88.6 |
| 95 | 0.392 | 0.393 | 0.872 | 91.1 |
| 96 | 0.392 | 0.393 | 0.875 | 92.6 |
| 101 | 0.392 | 0.393 | 0.867 | 89.8 |
| 105 | 0.392 | 0.393 | 0.875 | 89.5 |
| 108 | 0.393 | 0.393 | 0.893 | 89.6 |
| 110 | 0.391 | 0.398 | 0.857 | 87.8 |

We use capacitor

Chapter Eight : Economical Study

Economical study o f p.f improvement

∆p before adding capacitor = 0.808 Mw

∆p after adding capacitor  = 0.790 Mw

∆∆p = ∆p before - ∆p after = 0.808 – 0.790 = 0.018 Mw

Z∆p =  ∆∆p*T*cost/MWh

We take tmax = 5550 h , then we calculate T

T=8760(0.124+0.0001tmax)^2

T=4000 hour

 Z∆p = 0.018*4000*140 = 10080$

Now we calculate cost of capacitors :

Zc = Qc*Cc ( fixed & regulated)* EH( capital recovery factor )

We know that the cost of the capacitor is as follow:-

Fixed Cap=5000 $/Mvar

Regulated Cap=15000  $/Mvar

 Zc = 1.8*5000*0.22 = 1980$

Saving in P.f  penalties :

Saving in p.f = ( 0.92-0.86)*11.3*4000*140 *0.02 = 7593$

Total saving =  saving in Δp +saving in power factor – Zc

=  10080 + 7593 – 1980 = 15693 $

S.P.B.P =  investment   =     1.8*5000   =  0.57 year

Annual saving        15693

=  0.57 year *12 =  6.78 months .

influence of Load factor correction .

Some transformers are over loaded T16,T22,T32… while others are operating at light load  as T7,T26 , T42 .

To have a good transformer loading the load factor should be greater than 0.6 In order to make the transformer works on a better efficiency …

We make the following correction and we show the influence

|  | T16 | T22 | T32 | T7 | T26 | T42 |
| --- | --- | --- | --- | --- | --- | --- |
| L.F before | 97 | 96 | 98 | 34 | 41 | 38 |
| L.F after | 65 | 53 | 64 | 59 | 60 | 70 |
| Voltage before | 387 | 393 | 387 | 394 | 388 | 393 |
| Voltage after | 391 | 390 | 391 | 392 | 392 | 389 |

And we save :

3KW and 17 Kvar

Chapter NINE:

Connection with west bank net work :

We connect the Jericho net work to the west bank net work to study the effect of its connection on Jericho net work.

We want to study the change of buses voltage , current of feeders , power factor and losses .

Information of west bank net work :

| Bus | P+jQ (MVA) | S (MVA) | PF |
| --- | --- | --- | --- |
| 0 | 15.8+j5.83 | 16.84 | 0.94 |
| 1 | 34.8+j8.2 | 35.75 | 0.97 |
| 2 | 62.4+j16.1 | 64.44 | 0.96 |
| 3 | 7.8+j2.5 | 8.2 | 0.95 |
| 4 | 30+j7.59 | 30.95 | 0.97 |
| 5 | 6.2+j0.9 | 6.26 | 0.98 |
| 6 | 88.6+j24.6 | 91.95 | 0.96 |
| 7 | 16.6+j4.5 | 17.2 | 0.96 |
| 8 | 108.5+j31.22 | 112.9 | 0.96 |
| 9 | 60.8+j16.77 | 63.07 | 0.96 |
| 10 | 92.6+j24.47 | 95.77 | 0.97 |

| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Qal | Tul | Nab | Tub | Jen | Sil | Ram | Jer | Jur | Bet | Heb |

| Line | power flow (MW) | L (Km) | V calc (KV) | V standard (KV) |
| --- | --- | --- | --- | --- |
| A-1 | 119.5 | 25 | 156.25 | 230 |
| A-2 | 164.7 | 31 | 166.7 | 230 |
| 1_2 | 84.7 | 25 | 143 | 230 |
| 2_3 | 38.7 | 20 | 105.7 | 132 |
| 3_4 | 30 | 29 | 100 | 132 |
| 2_5 | 148.3 | 28 | 169.5 | 230 |
| 5_6 | 142.1 | 24 | 161.3 | 230 |
| 7_6 | 67 | 35 | 139 | 230 |
| 6_8 | 261.9 | 18 | 164 | 230 |
| 7_8 | 141.4 | 32 | 172.4 | 230 |
| 8_9 | 153.4 | 10.3 | 124 | 132 |
| 9_10 | 92.6 | 16.5 | 132.3 | 132 |

| Bus | S (MVA) | Scalc | S rated | type of T | rated v |
| --- | --- | --- | --- | --- | --- |
| 0 | 300 | 214.2857 | 250 | 3 | 230/11/22 |
| 1 | 37.51 | 26.79286 | 40 | 2 | 230/22 |
| 2 | 107.24 | 76.6 | 125 | 3 | 230/132/33 |
| 3 | 8.19 | 5.85 | 16 | 2 | 132/33 |
| 4 | 31.83 | 22.73571 | 32 | 2 | 132/33 |
| 5 | 6.26 | 4.471429 | 16 | 2 | 230/33 |
| 6 | 94.9 | 67.78571 | 80 | 2 | 230/33 |
| 7 | 16.6 | 11.85714 | 16 | 2 | 230/33 |
| 8 | 281.1 | 200.7857 | 250 | 3 | 230/132/33 |
| 9 | 64.9 | 46.35714 | 63 | 2 | 132/33 |
| 10 | 99.5 | 71.07143 | 160 | 2 | 132/33 |

| Line | P+jQ (MVA) | S | V standard (KV) | If | Inom | Fecon | Imax |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A-1 | 119.5+j49.2 | 129.23 | 230.00 | 777.25 | 324.41 | 555.18 | 1050 |
| A-2 | 164.7+j72.8 | 180.07 | 230.00 | 769.36 | 452.03 | 549.54 | 1050 |
| 1_2 | 84.7+j0.03 | 84.70 | 230.00 | 688.91 | 212.62 | 492.08 | 960 |
| 2_3 | 38.7+j10 | 39.97 | 132.00 | 174.83 | 87.41 | 124.88 | 450 |
| 3_4 | 30+j7.59 | 30.95 | 132.00 | 135.38 | 67.69 | 96.70 | 390 |
| 2_5 | 148.3+j87.58 | 172.23 | 230.00 | 432.35 | 216.17 | 308.82 | 730 |
| 5_6 | 142.1+j86.7 | 166.46 | 230.00 | 417.86 | 208.93 | 298.47 | 710 |
| 6_7 | 67+j9.3 | 67.64 | 230.00 | 169.80 | 524.36 | 121.28 | 450 |
| 6_8 | 261.9+j72.1 | 271.64 | 230.00 | 681.90 | 524.36 | 487.07 | 960 |
| 7_8 | 141.4+j19.5 | 142.74 | 230.00 | 358.32 | 682.76 | 255.94 | 710 |
| 8_9 | 153.4+j59.24 | 164.44 | 132 | 719.2596 | 359.6298 | 513.7568 | 1050 |
| 9_10 | 92.6+j36.47 | 99.52 | 132 | 435.2999 | 217.6499 | 310.9285 | 730 |

The result after connection :

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW               Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):             254.144                 76.511               256.411             95.8 Lagging

Generators:                276.00               117.6                300.01                    92.0  Lagging

Total Demand:         530.144                 194.111              564.563           93.9  Lagging

1.max load :

| Bus # | Voltage nom | Voltage Before conn. | Voltage after conn |
| --- | --- | --- | --- |
| 2 | 0.400 | 0.391 | 0.385 |
| 5 | 0.400 | 0.385 | 0.385 |
| 6 | 0.400 | 0.383 | 0.385 |
| 7 | 0.400 | 0.384 | 0.385 |
| 8 | 0.400 | 0.386 | 0.385 |
| 9 | 0.400 | 0.384 | 0.385 |
| 10 | 0.400 | 0.384 | 0.379 |
| 13 | 0.400 | 0.385 | 0.379 |
| 15 | 0.400 | 0.385 | 0.379 |
| 18 | 0.400 | 0.375 | 0.379 |
| 19 | 0.400 | 0.384 | 0.379 |
| 20 | 0.400 | 0.382 | 0.379 |
| 22 | 0.400 | 0.382 | 0.379 |
| 24 | 0.400 | 0.380 | 0.375 |
| 25 | 0.400 | 0.384 | 0.375 |
| 28 | 0.400 | 0.385 | 0.375 |
| 31 | 0.400 | 0.385 | 0.375 |
| 32 | 0.400 | 0.378 | 0.375 |
| 33 | 0.400 | 0.379 | 0.375 |
| 36 | 0.400 | 0.386 | 0.375 |
| 38 | 0.400 | 0.386 | 0.380 |
| 40 | 0.400 | 0.385 | 0.380 |
| 41 | 0.400 | 0.386 | 0.380 |
| 42 | 0.400 | 0.384 | 0.380 |
| 48 | 0.400 | 0.381 | 0.380 |
| 52 | 0.400 | 0.381 | 0.380 |
| 59 | 0.400 | 0.382 | 0.380 |
| 62 | 0.400 | 0.381 | 0.380 |
| 63 | 0.400 | 0.373 | 0.375 |
| 65 | 0.400 | 0.372 | 0.375 |
| 70 | 0.400 | 0.382 | 0.375 |
| 72 | 0.400 | 0.379 | 0.375 |
| 73 | 0.400 | 0.379 | 0.375 |
| 74 | 0.400 | 0.378 | 0.375 |
| 81 | 0.400 | 0.379 | 0.375 |
| 82 | 0.400 | 0.381 | 0.375 |
| 83 | 0.400 | 0.379 | 0.375 |
| 85 | 0.400 | 0.377 | 0.375 |
| 92 | 0.400 | 0.379 | 0.375 |
| 95 | 0.400 | 0.380 | 0.380 |
| 96 | 0.400 | 0.380 | 0.380 |
| 101 | 0.400 | 0.381 | 0.380 |
| 105 | 0.400 | 0.380 | 0.380 |
| 108 | 0.400 | 0.382 | 0.380 |
| 110 | 0.400 | 0.379 | 0.380 |

2. Min load :

| Bus # | Voltage nom | Voltage Before conn | Voltage after conn |
| --- | --- | --- | --- |
| 2 | 0.400 | 0.396 | 0.392 |
| 5 | 0.400 | 0.394 | 0.392 |
| 6 | 0.400 | 0.393 | 0.392 |
| 7 | 0.400 | 0.395 | 0.392 |
| 8 | 0.400 | 0.394 | 0.392 |
| 9 | 0.400 | 0.393 | 0.392 |
| 10 | 0.400 | 0.394 | 0.391 |
| 13 | 0.400 | 0.394 | 0.391 |
| 15 | 0.400 | 0.394 | 0.391 |
| 18 | 0.400 | 0.390 | 0.391 |
| 19 | 0.400 | 0.393 | 0.391 |
| 20 | 0.400 | 0.393 | 0.391 |
| 22 | 0.400 | 0.393 | 0.391 |
| 24 | 0.400 | 0.392 | 0.391 |
| 25 | 0.400 | 0.393 | 0.391 |
| 28 | 0.400 | 0.391 | 0.391 |
| 31 | 0.400 | 0.394 | 0.391 |
| 32 | 0.400 | 0.391 | 0.391 |
| 33 | 0.400 | 0.391 | 0.391 |
| 36 | 0.400 | 0.394 | 0.390 |
| 38 | 0.400 | 0.393 | 0.390 |
| 40 | 0.400 | 0.394 | 0.390 |
| 41 | 0.400 | 0.394 | 0.390 |
| 42 | 0.400 | 0.394 | 0.390 |
| 48 | 0.400 | 0.392 | 0.390 |
| 52 | 0.400 | 0.392 | 0.390 |
| 59 | 0.400 | 0.393 | 0.390 |
| 62 | 0.400 | 0.392 | 0.390 |
| 63 | 0.400 | 0.389 | 0.390 |
| 65 | 0.400 | 0.389 | 0.391 |
| 70 | 0.400 | 0.393 | 0.391 |
| 72 | 0.400 | 0.392 | 0.391 |
| 73 | 0.400 | 0.392 | 0.391 |
| 74 | 0.400 | 0.391 | 0.391 |
| 81 | 0.400 | 0.392 | 0.391 |
| 82 | 0.400 | 0.392 | 0.391 |
| 83 | 0.400 | 0.391 | 0.391 |
| 85 | 0.400 | 0.391 | 0.391 |
| 92 | 0.400 | 0.391 | 0.391 |
| 95 | 0.400 | 0.392 | 0.390 |
| 96 | 0.400 | 0.392 | 0.390 |
| 101 | 0.400 | 0.392 | 0.390 |
| 105 | 0.400 | 0.392 | 0.390 |
| 108 | 0.400 | 0.393 | 0.390 |
| 110 | 0.400 | 0.391 | 0.390 |

Compression between before and after connection :

|  | Before | After |
| --- | --- | --- |
| Current (A) | 262 | 317 |
| Losses | 5% | 6.05% |

References:

- Jerusalem district electricity co.

- Palestine Central Bureau of Statistics Website.

- Dr. Maher J. Khammash

Design of an Electrical Network for the West Bank of Palestine with the Selection of Optimum Site of the Generating Power Plant