Chapter One :

Palestine Network

1.1  Electricity status in Palestine:

Due to the Israeli occupation Palestine has not yet a unified power system; the existing networks are local low voltage distribution networks.

The main supply for electrical distribution networks in the West Bank and Gaza is the Israeli Electrical Company (IEC).

The voltages of the existing distribution networks are 0.4, 6.6, 11, 22 , and 33 KV . IEC supplies electricity to the electrified communities by 22 or 33 KV by overhead lines . Electricity is purchased from IEC and then distributed to the consumers.

The results of the survey indicated that 99.6%of households in the Palestinian Territory were connected to the public electricity network in April 2008 , where this percentage was 99.3% during April 2006, and was 97.2% during July 2005, while it was 97.2% during the same month1999 .  0.3% have no electricity services, 0.1% of the households have their own generators.

From the results of the survey, it is noted that south of the West Bank has the lowest percentage of households connected to electricity network (99.0%). The situation is different in Gaza Strip which has 99.6% of the households connected to electricity network during April 2006.

1.2  Purchases of Electrical Energy

Due to the Palestinian Central Bureau of Statistics during 2006 , total electrical energy purchases in the Palestinian Territory reached 3,441,700 MWh; 2,331,110 MWh in the West Bank and 1,110,590 MWh in Gaza Strip(765,290 MWh imported from Israel and 345,300 MWh produced by Gaza Power Plant).

1.3 Household Consumption of electricity

The results of the survey indicated that the average household electricity consumption (from the households that used electricity) in the Palestinian Territory during April2008 was 282 KWh.

While during April2006 was 211 KWh, where this average was 380.1 KWh during July 2005, and it was 380.1KWh during the same month 1999. This average ranged by region and type of locality in April 2008, it reached 367 KWh in the Middle of the West Bank and didn’t exceed 217 KWh in the North of West Bank. This average was about 293 KWh in urban localities and 205 KWh in rural localities, and 357 KWh in refugee camps.

And the average per capita electricity consumption in the Palestinian Territory during April 2008 was 48.6 KWh.

While during April 2006 was 39.7 KWh.

1.4 Electrical Sources and Network problems

There are many problems that the consumer face it in the network.

The level of electrical services provided by the IEC is inadequate, which constitutes a handicap for the industrial sector, high economic losses, and an obstacle for the development of the country. With an electricity consumption level of 583 kWh/person (1999), the lowest consumption level in the region , the Palestinian Territories barely manage to satisfy their electric needs, whereas in Israel electricity consumption exceeds 6000 kWh/person.

This gap can be mainly explained by an inadequate electricity

Infra structure, high transmission losses (25%) and high electricity prices.

Palestinian electricity consumption appears to be inelastic. However, the Palestinian electricity sector shows a high vulnerability to political shocks. The influence of conflict on

the electricity sector goes beyond direct destruction. It results in a modification of the

trajectory of electricity consumption, a deceleration in the growth rate, and the retardation of a “healthy” recovery.

Electricity problems and priorities can be summarized as follows:

The lack of investment and public expenditure, high prices, and high transmission losses constitute fundamental problems for the electricity sector. The quality of the electrical services is inadequate and below standard.

Another problem that the Israeli Electricity Corporation (IEC) imposes the municipalities and large consumer in Palestine to pay penalties if they cause a power factor less than 0.92 . The Jerusalem Electricity company (JEDCO) is the only company that imposes the three phase industrial consumers with PF penalties if their PF is less than 0.92 . On other hand , several municipalities in the West Bank and Gaza strip are in the process of imposing power factor penalties on industrial customers with low PF .

Table below show relation of PF to the penalties

| PF | penalties |
| --- | --- |
| 0.92 or more | No penalties |
| Less than 0.92 to 0.8 | 1%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.8 to 0.7 | 1.25%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.7 | 1.5%of the total bill for every 0.01 of PF less than 0.92 |

1.5 Energy consumption in different sector    in Palestine

Electricity utilization is considered essential not only for the industrial and residential sectors, but also for water pumping and street lights. Data from the Palestinian Energy Authority for

electricity consumption indicates that the residential sector consumes (50 – 60)% of the total electricity against (12 – 14) % for the commercial sector and (10 – 12)% for industrial sector . Electricity consumption for both water pumping and street lights is 15% , (3 – 4)% respectively .

It can be shown as a table below:

| Type of sector | Percentage |
| --- | --- |
| Residential sector | (50 – 60)% |
| Industrial sector | (12 – 14) % |
| Commercial sector | (10 – 12)% |
| Water pumping | 15% |
| Street lighting | (3 – 4)% |

Chapter two

Qalqilia Network

2.1 Introduction to Qalqilia Network

Qalqilia electrical distribution network is fed from one connection point by the Israel Electrical Company (IEC)  , at 22 KV .

The development of electrical energy purchased from I.E.C. and  growth rate are :

| Year | Annual Purchased M.W.H | Growth Rate % |
| --- | --- | --- |
| 2002 | 34727.4 | 0 |
| 2003 | 34727.4 | 0 |
| 2004 | 37273.8 | 7.3 |
| 2005 | 39264.8 | 5.34 |
| 2006 | 44708.0 | 13.86 |
| 2007 | 50830.96 | 13.7 |

The energy consumed is distributed into different types  :

| Type of load | Consumption |
| --- | --- |
| Residential | 77.83 % |
| Commercial | 15.61 % |
| Industrial | 2.84 % |
| Agricultural | 2.14 % |
| Organization | 1.58 % |

The change of losses in the Qalqilia electrical distribution network as shown in the  table  :

| Year | ∆p % |
| --- | --- |
| 1995 | 15 % |
| 1996 | 14 % |
| 1997 | 10 % |
| 1998 | 9 % |

But in 2008 it decreases to reach about  3  %  for max case .

2.2 Elements Of The Network :

1. Electrical Supply:

One connection point at 22 kV from IEC .

The peak power consumption is 11.804 MW

2. Medium voltage lines (Transmission line):

There are two type of conductor :

- The Over Head Lines :

The Over Head Lines used in the network are  22KV , ACSR (Aluminum conductor steel reinforced )

With two cross sectional areas ( 50mm2 called Rabbit ,         95mm2  called Dog ) .

- Under ground cables :

Under ground cables used in the network are

22KV , XLPE , 240mm2Cu ,

150mm2Cu , 120 mm2AL , 95mm2AL.

The resistance / km and reactance / km  and max current for all T.L ( Over head  lines and under ground cables ) as shown :

| Type of T.L | Resistance Ohms/Km | Reactance Ohms/Km | Max current capacity (A) |
| --- | --- | --- | --- |
| O.H.L Rabbit 50 mm2 | 0.543 | 0.333 | 174 |
| O.H.L Dog 95 mm2 | 0.301 | 0.332 | 250 |
| UGC Al 95 mm2 | 0.41 | 0.121 | 250 |
| UGC Cu 120 mm2 | 0.196 | 0.117 | 360 |
| UGC Cu 150 mm2 | 0.159 | 0.114 | 410 |

3. Distribution Transformers :

Number of distribution transformers in   Qalqilia  network are 49 .

All transformer   22KV / 0.4KV  Δ-Υ connected , distribution transformers with ratings 630 , 400 , 250 KVA .

| Transformer Ratings KVA | No. of Transformers |
| --- | --- |
| 630 | 18 |
| 400 | 29 |
| 250 | 2 |

2.3   Problems  in  Qalqilia  network :

- the main T.L coming from the connection point is  Rabbit ( 50 mm2  ) did not have the capability to hold the over current resulting in cutting off the supply on the maximum load condition , because total current pass from this line equal 344 A but max capacity current of this line is 174 A.

- Bad distribution of the loads on the existing Transformers which cause a poor load factor , because there are some transformers work at max load factor more than 100 % and some transformers work with load factor less than 60 % .

Note that the transformer work with max efficiency when load factor between ( 65-75 ) %.

Solution: change the configuration of some branches and transformers  .

- One connection point and this lead to make the performance of the  network  weak .

( no reliability in network  )

Solution: it is very important to get another connection point to supply the city .

- High drop voltage : this effect on the losses in the network and on the power factor  .

Solution: use capacitor banks ( fixed or variable )

Chapter three

Load Flow Analysis

3.1 Load flow study :

In power engineering, the power flow study (also known as load-flow study) is an important tool involving numerical analysis applied to a power system. Unlike traditional circuit analysis, a power flow study usually uses simplified notation such as a one-line diagram and per-unit system, and focuses on various forms of AC power (ie: reactive, real, and apparent) rather than voltage and current. It analyses the power systems in normal steady-state operation. There exist a number of software implementations of power flow studies.

In addition to a power flow study itself, sometimes called the base case, many software implementations perform other types of analysis, such as short-circuit fault analysis and economic analysis. In particular, some programs use linear programming to find the optimal power flow, the conditions which give the lowest cost per kilowatt generated.

The great importance of power flow or load-flow studies is in the planning the future expansion of power systems as well as in determining the best operation of existing systems. The principal information obtained from the power flow study is the magnitude and phase angle of the voltage at each bus and the real and reactive power flowing in each line.

In our project we use the ETAP software to analyze Qalqilia network .

3.2 ETAP Power Station Program:

With ETAP’s advanced Load Flow module, you can create and validate your system model with ease and obtain accurate and reliable results. Built-in features like automatic device evaluation, summary alarms / warnings, result analyzer, and intelligent graphics make it the most efficient Load Flow program available today.

ETAP calculates bus voltages, branch power factors, currents, and power flows throughout the electrical system. ETAP allows for swing, voltage regulated, and unregulated power sources with multiple power grids and generator connections. It is capable of performing analysis on both radial and loop systems. ETAP allows you to select from several different methods in order to achieve the best calculation efficiency and accuracy.

]

Features of ETAP:

- Newton-Raphson , fast decoupled, & accelerated 
Gauss Seidel

- Generator governors with isochronous or droop mode

- Generator exciters with AVR or Mvar / PF controllers

- Transformer load tap changers (LTC / regulators)

- Advanced solution techniques for fast convergence

- Multiple loading conditions

- Multiple generation conditions

- Swing, voltage regulated, & unregulated power sources

- Voltage drop calculations

- Load forecasting

- Alert view to display critical & marginal limit violations

- Bus / transformer / cable overload warning

- Single-phase load flow display

- Global & individual bus diversity factors

- Individual demand factors for continuous, intermittent, 
& spare operating conditions

- Option to update the initial condition from load flow solutions

- Phase-shifting transformer

- Power factor correction

- Multi-report result analyzer

- 10,000+ bus capability

3.3 In our project we do the following steps:

Step1: collection of data which consist of :

- Actual loads on transformer and power factor .

- Impedances of transmission lines ( R, X) .

Step2: Plotting the one line diagram in ETAP .

Step 3: Analysis and study the maximum and minimum        case.

Step 4: improvement of power factor .

Step 5: improvement of voltages level by the following scenarios:

- Rise the swing bus about 105% .

- Using capacitor banks (fixed and regulated) .

- Putting two connection points ( without ring and with ring ) .

- Changing the main transmission line of the network .

- Load factor corrections .

Step 6: economical study .

Step 7: Low Tension analysis .

Table of transformers’ loading

| Transformer | S RATED KVA | S ACTUAL KVA | LF % |
| --- | --- | --- | --- |
| 1 | 400 | 298 | 74.5 |
| 2 | 400 | 414 | 103.6 |
| 3 | 630 | 375 | 59.6 |
| 4 | 630 | 344 | 54.5 |
| 5 | 400 | 198 | 49.4 |
| 6 | 400 | 261 | 65.4 |
| 7 | 400 | 380 | 95 |
| 8 | 400 | 402 | 100.5 |
| 9 | 250 | 179 | 71.5 |
| 10 | 630 | 358 | 56.9 |
| 11 | 630 | 358 | 56.6 |
| 12 | 400 | 235 | 58.6 |
| 13 | 400 | 145 | 36.2 |
| 14 | 630 | 224 | 35.6 |
| 15 | 400 | 148 | 37.0 |
| 16 | 630 | 287 | 45.5 |
| 17 | 400 | 198 | 49.4 |
| 18 | 630 | 263 | 41.7 |
| 19 | 630 | 295 | 46.9 |
| 20 | 630 | 373 | 59.3 |
| 21 | 400 | 210 | 52.4 |
| 22 | 400 | 271 | 67.6 |
| 23 | 400 | 382 | 82.0 |
| 24 | 400 | 205 | 51.4 |
| 25 | 400 | 198 | 49.4 |
| 26 | 400 | 248 | 61.9 |
| 27 | 400 | 248 | 61.9 |
| 28 | 400 | 169 | 42.3 |
| 29 | 400 | 211 | 52.7 |
| 30 | 400 | 224 | 56.0 |
| 31 | 400 | 224 | 55.9 |
| 32 | 400 | 134 | 33.5 |
| 33 | 400 | 146 | 36.5 |
| 34 | 630 | 242 | 38.4 |
| 35 | 250 | 148 | 59.2 |
| 36 | 400 | 264 | 66.0 |
| 37 | 400 | 195 | 48.6 |
| 38 | 400 | 228 | 57.0 |
| 39 | 630 | 249 | 39.6 |
| 40 | 630 | 208 | 33.0 |
| 41 | 630 | 369 | 58.6 |
| 42 | 400 | 252 | 62.9 |
| 43 | 630 | 320 | 50.8 |
| 44 | 400 | 211 | 52.7 |
| 45 | 400 | 193 | 48.2 |
| 46 | 630 | 467 | 74.1 |
| 47 | 630 | 272 | 43.2 |
| 48 | 630 | 300 | 47.7 |
| 49 | 630 | 326 | 51.7 |

Before improvement (original case)

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):           11.804               5.684               13.101              90.1  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         11.804            5.684               13.101               90.1  Lagging

---------     ---------     ---------     --------------

Total Motor Load:           0.000                0.000                   0.000                 100.0  Lagging

Total Static Load:         11.444         4.988

Apparent Losses:            0.360         0.696

Total current  344 A .

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| 2 | 0.400 | 0.391 | 0.26 | 0.11 | 91.8 |
| 5 | 0.400 | 0.385 | 0.41 | 0.19 | 91.0 |
| 6 | 0.400 | 0.383 | 0.26 | 0.12 | 91.1 |
| 7 | 0.400 | 0.384 | 0.19 | 0.08 | 91.4 |
| 8 | 0.400 | 0.386 | 0.18 | 0.08 | 91.4 |
| 9 | 0.400 | 0.384 | 0.20 | 0.09 | 91.8 |
| 10 | 0.400 | 0.384 | 0.23 | 0.11 | 90.7 |
| 11 | 0.400 | 0.385 | 0.19 | 0.08 | 91.7 |
| 12 | 0.400 | 0.385 | 0.26 | 0.12 | 90.9 |
| 13 | 0.400 | 0.375 | 0.36 | 0.17 | 90.9 |
| 14 | 0.400 | 0.384 | 0.27 | 0.13 | 90.1 |
| 15 | 0.400 | 0.382 | 0.65 | 0.27 | 92.4 |
| 16 | 0.400 | 0.382 | 0.18 | 0.08 | 90.8 |
| 17 | 0.400 | 0.380 | 0.53 | 0.27 | 90.1 |
| 18 | 0.400 | 0.384 | 0.13 | 0.06 | 90.7 |
| 20 | 0.400 | 0.385 | 0.16 | 0.07 | 91.4 |
| 21 | 0.400 | 0.385 | 0.14 | 0.05 | 94.1 |
| 22 | 0.400 | 0.378 | 0.23 | 0.13 | 87.9 |
| 23 | 0.400 | 0.379 | 0.29 | 0.12 | 92.4 |
| 24 | 0.400 | 0.386 | 0.20 | 0.08 | 92.6 |
| 26 | 0.400 | 0.386 | 0.29 | 0.12 | 91.7 |
| 28 | 0.400 | 0.385 | 0.13 | 0.05 | 93.3 |
| 29 | 0.400 | 0.386 | 0.13 | 0.04 | 94.7 |
| 30 | 0.400 | 0.384 | 0.25 | 0.10 | 93.0 |
| 31 | 0.400 | 0.381 | 0.45 | 0.19 | 92.2 |
| 32 | 0.400 | 0.381 | 0.34 | 0.14 | 93.3 |
| 34 | 0.400 | 0.382 | 0.29 | 0.12 | 92.4 |
| 35 | 0.400 | 0.381 | 0.20 | 0.09 | 92.1 |
| 36 | 0.400 | 0.373 | 0.33 | 0.15 | 93.1 |
| 37 | 0.400 | 0.372 | 0.35 | 0.16 | 91.4 |
| 38 | 0.400 | 0.382 | 0.22 | 0.10 | 91.3 |
| 39 | 0.400 | 0.379 | 0.34 | 0.13 | 93.7 |
| 40 | 0.400 | 0.379 | 0.14 | 0.05 | 93.7 |
| 42 | 0.400 | 0.378 | 0.20 | 0.10 | 88.9 |
| 43 | 0.400 | 0.379 | 0.19 | 0.09 | 90.9 |
| 45 | 0.400 | 0.381 | 0.15 | 0.06 | 92.8 |
| 46 | 0.400 | 0.379 | 0.19 | 0.09 | 92.8 |
| 48 | 0.400 | 0.377 | 0.24 | 0.10 | 92.6 |
| 49 | 0.400 | 0.379 | 0.17 | 0.08 | 90.0 |
| 50 | 0.400 | 0.380 | 0.17 | 0.07 | 92.2 |
| 51 | 0.400 | 0.380 | 0.22 | 0.11 | 89.5 |
| 52 | 0.400 | 0.381 | 0.31 | 0.12 | 93.1 |
| 54 | 0.400 | 0.380 | 0.24 | 0.09 | 93.4 |
| 55 | 0.400 | 0.382 | 0.36 | 0.15 | 92.7 |
| 56 | 0.400 | 0.379 | 0.22 | 0.11 | 90.1 |

Raise the swing voltage from 22 kV to 23.1 kV

We raise voltages of the swing bus to 105% of its rated voltage

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW           Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):           13.127               6.321               14.519              90.1  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         13.127               6.321               14.519              90.1  Lagging

---------     ---------     ---------     --------------

Total Motor Load:           0.000                0.000                   0.000                 100.0  Lagging

Total Static Load:         12.727         5.547

Apparent Losses:            0.400         0.773

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.412 | 0.29 | 0.12 | 91.8 |
| Bus5 | 0.400 | 0.406 | 0.46 | 0.21 | 91.0 |
| Bus6 | 0.400 | 0.403 | 0.29 | 0.13 | 91.1 |
| Bus7 | 0.400 | 0.408 | 0.21 | 0.09 | 91.4 |
| Bus8 | 0.400 | 0.405 | 0.20 | 0.09 | 91.4 |
| Bus9 | 0.400 | 0.405 | 0.22 | 0.10 | 91.8 |
| Bus10 | 0.400 | 0.407 | 0.26 | 0.12 | 90.7 |
| Bus11 | 0.400 | 0.405 | 0.21 | 0.09 | 91.7 |
| Bus12 | 0.400 | 0.406 | 0.29 | 0.13 | 90.9 |
| Bus13 | 0.400 | 0.395 | 0.40 | 0.18 | 90.9 |
| Bus14 | 0.400 | 0.405 | 0.29 | 0.14 | 90.1 |
| Bus15 | 0.400 | 0.403 | 0.72 | 0.30 | 92.4 |
| Bus16 | 0.400 | 0.403 | 0.20 | 0.09 | 90.8 |
| Bus17 | 0.400 | 0.401 | 0.59 | 0.28 | 90.1 |
| Bus18 | 0.400 | 0.405 | 0.14 | 0.09 | 90.7 |
| Bus20 | 0.400 | 0.399 | 0.18 | 0.08 | 91.4 |
| Bus21 | 0.400 | 0.405 | 0.15 | 0.05 | 94.1 |
| Bus22 | 0.400 | 0.398 | 0.26 | 0.14 | 87.9 |
| Bus23 | 0.400 | 0.399 | 0.33 | 0.13 | 92.4 |
| Bus24 | 0.400 | 0.407 | 0.23 | 0.09 | 92.6 |
| Bus26 | 0.400 | 0.404 | 0.32 | 0.14 | 91.7 |
| Bus28 | 0.400 | 0.406 | 0.15 | 0.06 | 93.3 |
| Bus29 | 0.400 | 0.407 | 0.14 | 0.05 | 94.7 |
| Bus30 | 0.400 | 0.405 | 0.28 | 0.11 | 93.0 |
| Bus31 | 0.400 | 0.402 | 0.50 | 0.21 | 92.2 |
| Bus32 | 0.400 | 0.402 | 0.38 | 0.16 | 92.3 |
| Bus34 | 0.400 | 0.403 | 0.33 | 0.14 | 92.4 |
| Bus35 | 0.400 | 0.402 | 0.22 | 0.09 | 92.1 |
| Bus36 | 0.400 | 0.394 | 0.37 | 0.17 | 91.3 |
| Bus37 | 0.400 | 0.392 | 0.39 | 0.17 | 91.4 |
| Bus38 | 0.400 | 0.403 | 0.24 | 0.11 | 91.3 |
| Bus39 | 0.400 | 0.400 | 0.38 | 0.14 | 93.7 |
| Bus40 | 0.400 | 0.400 | 0.15 | 0.06 | 93.7 |
| Bus42 | 0.400 | 0.399 | 0.22 | 0.11 | 88.9 |
| Bus43 | 0.400 | 0.400 | 0.21 | 0.10 | 90.9 |
| Bus45 | 0.400 | 0.402 | 0.17 | 0.07 | 92.8 |
| Bus46 | 0.400 | 0.400 | 0.21 | 0.10 | 90.9 |
| Bus48 | 0.400 | 0.398 | 0.26 | 0.11 | 92.6 |
| Bus49 | 0.400 | 0.400 | 0.19 | 0.09 | 90.0 |
| Bus50 | 0.400 | 0.400 | 0.19 | 0.08 | 92.2 |
| Bus51 | 0.400 | 0.401 | 0.24 | 0.12 | 89.5 |
| Bus52 | 0.400 | 0.402 | 0.35 | 0.14 | 93.1 |
| Bus54 | 0.400 | 0.400 | 0.26 | 0.10 | 93.4 |
| Bus55 | 0.400 | 0.403 | 0.40 | 0.16 | 92.7 |
| Bus56 | 0.400 | 0.399 | 0.25 | 0.12 | 90.1 |

In this case all voltages above 392 volt

But we can't apply this method because the control of swing bus only by IEC .

CHAPTER 4:

POWER FACTOR IMPROVEMENT

As the Power Distribution network must be dimensioned to carry the apparent current, the optimum apparent current shall be maintained by improving the Power Factor close to unity. If appropriately sized capacitor banks or automatic systems are installed in parallel to the loads, the Reactive Current circulates between the capacitor and the load. This effectively means rest of the distribution network or the source is not subject to this additional Reactive Power. If Power Factor of unity is achieved by suitable combination of systems, the main current in the distribution is Active Power only .

Reactive Current circulating between the source and the load converts the electrical energy into heat. There is an additional load on the transformer, cables, switchgear etc., through the I2RT losses. This energy losses and voltage drops leads to additional loading on the source. If higher proportion of Reactive current is present, such losses will be higher and the distribution network shall have to be over sized to transmit Useful Power ‘P’ .

Effect of Low Power Factor

1. Higher Apparent Current.

Low Power Factor causes higher Apparent Current in any Load Centre.

2. Higher Losses in the Electrical Distribution System.

The loss in the Cables, Switches, Motors etc., are in square proportion of the Active Current leading to higher losses in the Electrical Systems. The higher Active Current passing through all electrical circuits, cables, bus bars, switches, motors etc., reduces the life of the components.

The electrical losses at a higher level will lead to higher resistive loss in square proportion of the Active Current, in turn leading to higher monthly consumption bills.

3.Low Voltage in the System.

The low power factor leads to low voltage which leads to motor winding burn-outs.

4. Low Plant Load Factor.

The low power factor reduces the capacity of the distribution network.

Low Power Factor increases the maintenance cost of the Power Distribution System.

Benefits of Improving Power Factor :

- Lower Apparent Power.

- Reduced KWH Losses.

- Improved Voltage leading to enhanced life of the transformer, cables, switchgear, motors etc., and lower energy cost.

Power factor correction by means of conventional capacitor banks will not be effective where the level of harmonics are higher. This is because the harmonic-currents are amplified in the parallel resonant circuit formed by the capacitor and the network. As a result, current and voltage distortion are further increased.

The first step is to raise the power factor to be 92% to avoid penalties .so we’ll add capacitors to meet this value of power factor.

Power factor improvement

PF old = 90 %

PF desired = 92%

We can obtain QC needed by the equation

Q c = Q old – Q new =P [tan cos-1(PF old) - tan cos-1(0.92)]

We’ll get Qc = 670 kVAr

Adding capacitors in delta connection parallel to the Transformer in secondary side (0.4 kV) .

POWER FACTOR IMPROVEMENT SUMMARY

MW	               Mvar	     MVA	% PF

Swing Bus            11.866               5.000        	12.876	92.20

Total Static Load:  11.520              4.327

Apparent Losses:    0.346             0.673

I Swing:		337 A

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.391 | 0.26 | 0.11 | 91.8 |
| Bus5 | 0.400 | 0.385 | 0.41 | 0.19 | 91.0 |
| Bus6 | 0.400 | 0.383 | 0.26 | 0.12 | 91.1 |
| Bus7 | 0.400 | 0.387 | 0.19 | 0.08 | 91.4 |
| Bus8 | 0.400 | 0.384 | 0.18 | 0.08 | 91.4 |
| Bus9 | 0.400 | 0.384 | 0.20 | 0.09 | 91.8 |
| Bus10 | 0.400 | 0.386 | 0.23 | 0.11 | 90.7 |
| Bus11 | 0.400 | 0.384 | 0.19 | 0.08 | 91.7 |
| Bus12 | 0.400 | 0.385 | 0.26 | 0.12 | 90.9 |
| Bus13 | 0.400 | 0.375 | 0.36 | 0.17 | 90.9 |
| Bus14 | 0.400 | 0.384 | 0.27 | 0.13 | 90.1 |
| Bus15 | 0.400 | 0.382 | 0.65 | 0.27 | 92.4 |
| Bus16 | 0.400 | 0.383 | 0.18 | 0.08 | 90.8 |
| Bus17 | 0.400 | 0.380 | 0.53 | 0.26 | 90.1 |
| Bus18 | 0.400 | 0.384 | 0.13 | 0.06 | 90.7 |
| Bus20 | 0.400 | 0.379 | 0.16 | 0.07 | 91.4 |
| Bus21 | 0.400 | 0.385 | 0.14 | 0.05 | 94.1 |
| Bus22 | 0.400 | 0.384 | 0.24 | 0.04 | 98.8 |
| Bus23 | 0.400 | 0.385 | 0.30 | 0.03 | 99.4 |
| Bus24 | 0.400 | 0.386 | 0.21 | 0.08 | 92.6 |
| Bus26 | 0.400 | 0.383 | 0.29 | 0.13 | 91.7 |
| Bus28 | 0.400 | 0.386 | 0.13 | 0.05 | 93.3 |
| Bus29 | 0.400 | 0.386 | 0.13 | 0.04 | 94.7 |
| Bus30 | 0.400 | 0.385 | 0.25 | 0.10 | 93.0 |
| Bus31 | 0.400 | 0.382 | 0.45 | 0.19 | 92.2 |
| Bus32 | 0.400 | 0.381 | 0.34 | 0.14 | 92.3 |
| Bus34 | 0.400 | 0.382 | 0.30 | 0.12 | 92.4 |
| Bus35 | 0.400 | 0.381 | 0.20 | 0.09 | 92.1 |
| Bus36 | 0.400 | 0.374 | 0.33 | 0.15 | 91.3 |
| Bus37 | 0.400 | 0.378 | 0.36 | 0.07 | 98.1 |
| Bus38 | 0.400 | 0.382 | 0.22 | 0.10 | 91.3 |
| Bus39 | 0.400 | 0.384 | 0.35 | 0.04 | 99.4 |
| Bus40 | 0.400 | 0.380 | 0.14 | 0.05 | 93.7 |
| Bus42 | 0.400 | 0.382 | 0.20 | 0.05 | 97.1 |
| Bus43 | 0.400 | 0.382 | 0.19 | 0.05 | 96.7 |
| Bus45 | 0.400 | 0.382 | 0.15 | 0.06 | 92.8 |
| Bus46 | 0.400 | 0.382 | 0.19 | 0.05 | 96.6 |
| Bus48 | 0.400 | 0.381 | 0.24 | 0.04 | 98.4 |
| Bus49 | 0.400 | 0.382 | 0.17 | 0.05 | 96.4 |
| Bus50 | 0.400 | 0.380 | 0.17 | 0.07 | 92.2 |
| Bus51 | 0.400 | 0.383 | 0.22 | 0.06 | 97.0 |
| Bus52 | 0.400 | 0.382 | 0.31 | 0.12 | 93.1 |
| Bus54 | 0.400 | 0.380 | 0.24 | 0.09 | 93.4 |
| Bus55 | 0.400 | 0.382 | 0.36 | 0.15 | 92.7 |
| Bus56 | 0.400 | 0.383 | 0.23 | 0.05 | 97.3 |

We note:

when we increase power factor the losses in the network decrease  .

Losses before p.f improvement = 0.360 Mw .

Losses after p.f improvement = 0.346 Mw .

Comparison between the original case and the case of power factor improvement

| Bus # | Voltage before | Voltage after | P.f before | p.f after |
| --- | --- | --- | --- | --- |
| bus2 | 0.391 | 0.391 | 91.8 | 91.8 |
| Bus5 | 0.385 | 0.385 | 91.0 | 91.0 |
| Bus6 | 0.383 | 0.383 | 91.1 | 91.1 |
| Bus7 | 0.384 | 0.387 | 91.4 | 91.4 |
| Bus8 | 0.386 | 0.384 | 91.4 | 91.4 |
| Bus9 | 0.384 | 0.384 | 91.8 | 91.8 |
| Bus10 | 0.384 | 0.386 | 90.7 | 90.7 |
| Bus11 | 0.385 | 0.384 | 91.7 | 91.7 |
| Bus12 | 0.385 | 0.385 | 90.9 | 90.9 |
| Bus13 | 0.375 | 0.375 | 90.9 | 90.9 |
| Bus14 | 0.384 | 0.384 | 90.1 | 90.1 |
| Bus15 | 0.382 | 0.382 | 92.4 | 92.4 |
| Bus16 | 0.382 | 0.383 | 90.8 | 90.8 |
| Bus17 | 0.380 | 0.380 | 90.1 | 90.1 |
| Bus18 | 0.384 | 0.384 | 90.7 | 90.7 |
| Bus20 | 0.385 | 0.379 | 91.4 | 91.4 |
| Bus21 | 0.385 | 0.385 | 94.1 | 94.1 |
| Bus22 | 0.378 | 0.384 | 87.9 | 98.8 |
| Bus23 | 0.379 | 0.385 | 92.4 | 99.4 |
| Bus24 | 0.386 | 0.386 | 92.6 | 92.6 |
| Bus26 | 0.386 | 0.383 | 91.7 | 91.7 |
| Bus28 | 0.385 | 0.386 | 93.3 | 93.3 |
| Bus29 | 0.386 | 0.386 | 94.7 | 94.7 |
| Bus30 | 0.384 | 0.385 | 93.0 | 93.0 |
| Bus31 | 0.381 | 0.382 | 92.2 | 92.2 |
| Bus32 | 0.381 | 0.381 | 93.3 | 92.3 |
| Bus34 | 0.382 | 0.382 | 92.4 | 92.4 |
| Bus35 | 0.381 | 0.381 | 92.1 | 92.1 |
| Bus36 | 0.373 | 0.374 | 93.1 | 91.3 |
| Bus37 | 0.372 | 0.378 | 91.4 | 98.1 |
| Bus38 | 0.382 | 0.382 | 91.3 | 91.3 |
| Bus39 | 0.379 | 0.384 | 93.7 | 99.4 |
| Bus40 | 0.379 | 0.380 | 93.7 | 93.7 |
| Bus42 | 0.378 | 0.382 | 88.9 | 97.1 |
| Bus43 | 0.379 | 0.382 | 90.9 | 96.7 |
| Bus45 | 0.381 | 0.382 | 92.8 | 92.8 |
| Bus46 | 0.379 | 0.382 | 92.8 | 96.6 |
| Bus48 | 0.377 | 0.381 | 92.6 | 98.4 |
| Bus49 | 0.379 | 0.382 | 90.0 | 96.4 |
| Bus50 | 0.380 | 0.380 | 92.2 | 92.2 |
| Bus51 | 0.380 | 0.383 | 89.5 | 97.0 |
| Bus52 | 0.381 | 0.382 | 93.1 | 93.1 |
| Bus54 | 0.380 | 0.380 | 93.4 | 93.4 |
| Bus55 | 0.382 | 0.382 | 92.7 | 92.7 |
| Bus56 | 0.379 | 0.383 | 90.1 | 97.3 |

CHAPTER 5:

THE IMPROVEMENT OF VOLTAGE LEVEL

Maximum load voltage level improvement

Adding capacitors (fixed and regulated) in delta connection parallel to the Transformer in secondary side (0.4 kv)

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW               Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):           12.015               3.174        12.427                    96.7 Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         11.804            5.684               13.101               90.1  Lagging

---------     ---------     ---------     --------------

Total Static Load:         11.691         2.547

Apparent Losses:            0.324         0.627

Total current  326 A .

We notice

when we improvement the voltage level the losses in the network decrease and the total current decrease

Losses in origin case   = 0.360 Mw

Losses after voltage improvement = 0.324 Mw

Total current in origin case = 344 A

Total current before voltage improvement = 326 A

Comparison between three  case

1.      the origin case .

2.      power factor improvement  case .

3.     voltage level improvement  case .

| Bus # | Voltage Origin case | Voltage Improve p.f | Voltage Improve of voltage level | P.f origin | p.f improve p.f | p.f Improve of voltage level |
| --- | --- | --- | --- | --- | --- | --- |
| bus2 | 0.391 | 0.391 | 0.395 | 91.8 | 91.8 | 99.80 |
| Bus5 | 0.385 | 0.385 | 0.389 | 91.0 | 91.0 | 97.43 |
| Bus6 | 0.383 | 0.383 | 0.389 | 91.1 | 91.1 | 99.45 |
| Bus7 | 0.384 | 0.387 | 0.390 | 91.4 | 91.4 | 97.15 |
| Bus8 | 0.386 | 0.384 | 0.387 | 91.4 | 91.4 | 97.17 |
| Bus9 | 0.384 | 0.384 | 0.387 | 91.8 | 91.8 | 97.04 |
| Bus10 | 0.384 | 0.386 | 0.390 | 90.7 | 90.7 | 99.77 |
| Bus11 | 0.385 | 0.384 | 0.387 | 91.7 | 91.7 | 97.23 |
| Bus12 | 0.385 | 0.385 | 0.388 | 90.9 | 90.9 | 97.07 |
| Bus13 | 0.375 | 0.375 | 0.381 | 90.9 | 90.9 | 97.76 |
| Bus14 | 0.384 | 0.384 | 0.387 | 90.1 | 90.1 | 96.46 |
| Bus15 | 0.382 | 0.382 | 0.385 | 92.4 | 92.4 | 96.47 |
| Bus16 | 0.382 | 0.383 | 0.387 | 90.8 | 90.8 | 98.90 |
| Bus17 | 0.380 | 0.380 | 0.386 | 90.1 | 90.1 | 99.01 |
| Bus18 | 0.384 | 0.384 | 0.387 | 90.7 | 90.7 | 98.42 |
| Bus20 | 0.385 | 0.379 | 0.383 | 91.4 | 91.4 | 97.70 |
| Bus21 | 0.385 | 0.385 | 0.385 | 94.1 | 94.1 | 94.10 |
| Bus22 | 0.378 | 0.384 | 0.385 | 87.9 | 98.8 | 98.81 |
| Bus23 | 0.379 | 0.385 | 0.386 | 92.4 | 99.4 | 99.42 |
| Bus24 | 0.386 | 0.386 | 0.387 | 92.6 | 92.6 | 92.60 |
| Bus26 | 0.386 | 0.383 | 0.385 | 91.7 | 91.7 | 95.58 |
| Bus28 | 0.385 | 0.386 | 0.386 | 93.3 | 93.3 | 93.30 |
| Bus29 | 0.386 | 0.386 | 0.387 | 94.7 | 94.7 | 94.70 |
| Bus30 | 0.384 | 0.385 | 0.385 | 93.0 | 93.0 | 93.00 |
| Bus31 | 0.381 | 0.382 | 0.384 | 92.2 | 92.2 | 95.83 |
| Bus32 | 0.381 | 0.381 | 0.384 | 93.3 | 92.3 | 95.53 |
| Bus34 | 0.382 | 0.382 | 0.387 | 92.4 | 92.4 | 99.46 |
| Bus35 | 0.381 | 0.381 | 0.386 | 92.1 | 92.1 | 98.85 |
| Bus36 | 0.373 | 0.374 | 0.380 | 93.1 | 91.3 | 98.32 |
| Bus37 | 0.372 | 0.378 | 0.379 | 91.4 | 98.10 | 98.10 |
| Bus38 | 0.382 | 0.382 | 0.385 | 91.3 | 91.3 | 98.15 |
| Bus39 | 0.379 | 0.384 | 0.384 | 93.7 | 99.4 | 99.40 |
| Bus40 | 0.379 | 0.380 | 0.386 | 93.7 | 93.7 | 99.40 |
| Bus42 | 0.378 | 0.382 | 0.383 | 88.9 | 97.1 | 97.15 |
| Bus43 | 0.379 | 0.382 | 0.383 | 90.9 | 96.7 | 96.65 |
| Bus45 | 0.381 | 0.382 | 0.384 | 92.8 | 92.8 | 96.92 |
| Bus46 | 0.379 | 0.382 | 0.383 | 92.8 | 96.6 | 96.61 |
| Bus48 | 0.377 | 0.381 | 0.381 | 92.6 | 98.4 | 96.82 |
| Bus49 | 0.379 | 0.382 | 0.383 | 90.0 | 96.4 | 96.43 |
| Bus50 | 0.380 | 0.380 | 0.383 | 92.2 | 92.2 | 97.80 |
| Bus51 | 0.380 | 0.383 | 0.384 | 89.5 | 97.0 | 96.99 |
| Bus52 | 0.381 | 0.382 | 0.386 | 93.1 | 93.1 | 99.49 |
| Bus54 | 0.380 | 0.380 | 0.384 | 93.4 | 93.4 | 98.81 |
| Bus55 | 0.382 | 0.382 | 0.384 | 92.7 | 92.7 | 95.66 |
| Bus56 | 0.379 | 0.383 | 0.383 | 90.1 | 97.3 | 97.29 |

From  the pervious table we notice that the buses voltage in the voltage level improvement  case the best of the three cases but we need to rise it more by another method.

In three cases there is a change in the current and losses

as shown in the next table :

|  | Origin case | power factor improvement case | voltage level improvement case |
| --- | --- | --- | --- |
| Total current | 344 A | 337 A | 326 A |
| Total losses | 0.36 Mw | 0.346 Mw | 0.324 Mw |

MINIMUM LOAD

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW               Mvar            MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):           4.911                  2.232               5.395                   91.0  Lagging

Generators:                0.000               0.000                0.000              100.0  Lagging

Total Demand:         4.911                  2.232               5.395                   91.0  Lagging

---------     ---------     ---------     --------------

Total Static Load:         4.850         2.114

Apparent Losses:            0.061         0.118

Total current  141 A .

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.396 | 0.106 | 0.046 | 91.77 |
| Bus5 | 0.400 | 0.394 | 0.173 | 0.079 | 91.00 |
| Bus6 | 0.400 | 0.393 | 0.111 | 0.050 | 91.10 |
| Bus7 | 0.400 | 0.395 | 0.078 | 0.035 | 91.40 |
| Bus8 | 0.400 | 0.394 | 0.077 | 0.034 | 91.40 |
| Bus9 | 0.400 | 0.393 | 0.085 | 0.037 | 91.80 |
| Bus10 | 0.400 | 0.394 | 0.098 | 0.045 | 90.70 |
| Bus11 | 0.400 | 0.394 | 0.080 | 0.035 | 91.70 |
| Bus12 | 0.400 | 0.394 | 0.110 | 0.051 | 90.90 |
| Bus13 | 0.400 | 0.390 | 0.156 | 0.072 | 90.90 |
| Bus14 | 0.400 | 0.393 | 0.112 | 0.054 | 90.10 |
| Bus15 | 0.400 | 0.393 | 0.274 | 0.113 | 92.39 |
| Bus16 | 0.400 | 0.393 | 0.074 | 0.034 | 90.80 |
| Bus17 | 0.400 | 0.392 | 0.225 | 0.109 | 90.08 |
| Bus18 | 0.400 | 0.393 | 0.054 | 0.025 | 90.70 |
| Bus20 | 0.400 | 0.391 | 0.068 | 0.030 | 91.40 |
| Bus21 | 0.400 | 0.394 | 0.058 | 0.021 | 94.10 |
| Bus22 | 0.400 | 0.391 | 0.099 | 0.054 | 87.90 |
| Bus23 | 0.400 | 0.391 | 0.125 | 0.052 | 92.40 |
| Bus24 | 0.400 | 0.394 | 0.086 | 0.035 | 92.60 |
| Bus26 | 0.400 | 0.393 | 0.121 | 0.053 | 91.70 |
| Bus28 | 0.400 | 0.394 | 0.056 | 0.022 | 93.30 |
| Bus29 | 0.400 | 0.394 | 0.052 | 0.018 | 94.70 |
| Bus30 | 0.400 | 0.394 | 0.104 | 0.041 | 93.00 |
| Bus31 | 0.400 | 0.392 | 0.189 | 0.079 | 92.18 |
| Bus32 | 0.400 | 0.392 | 0.143 | 0.060 | 92.30 |
| Bus34 | 0.400 | 0.393 | 0.125 | 0.052 | 92.40 |
| Bus35 | 0.400 | 0.392 | 0.085 | 0.036 | 92.10 |
| Bus36 | 0.400 | 0.389 | 0.145 | 0.065 | 91.30 |
| Bus37 | 0.400 | 0.389 | 0.154 | 0.068 | 91.40 |
| Bus38 | 0.400 | 0.393 | 0.092 | 0.041 | 91.30 |
| Bus39 | 0.400 | 0.392 | 0.146 | 0.054 | 93.70 |
| Bus40 | 0.400 | 0.392 | 0.058 | 0.022 | 93.70 |
| Bus42 | 0.400 | 0.391 | 0.085 | 0.044 | 88.90 |
| Bus43 | 0.400 | 0.392 | 0.079 | 0.036 | 90.90 |
| Bus45 | 0.400 | 0.392 | 0.065 | 0.026 | 92.80 |
| Bus46 | 0.400 | 0.391 | 0.080 | 0.037 | 90.90 |
| Bus48 | 0.400 | 0.391 | 0.102 | 0.042 | 92.60 |
| Bus49 | 0.400 | 0.391 | 0.073 | 0.035 | 90.00 |
| Bus50 | 0.400 | 0.392 | 0.074 | 0.031 | 92.20 |
| Bus51 | 0.400 | 0.392 | 0.093 | 0.046 | 89.50 |
| Bus52 | 0.400 | 0.392 | 0.133 | 0.052 | 93.10 |
| Bus54 | 0.400 | 0.392 | 0.101 | 0.039 | 93.40 |
| Bus55 | 0.400 | 0.393 | 0.152 | 0.062 | 92.65 |
| Bus56 | 0.400 | 0.391 | 0.094 | 0.045 | 90.10 |

VOLTAGE LEVEL IMPROVEMENT  of   MINIMUM LOAD

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):              4.931             1.676                  5.208                94.7  Lagging

Generators:                0.000               0.000                0.000                  100.0  Lagging

Total Demand:         4.931             1.676                  5.208                94.7  Lagging

---------     ---------     ---------     --------------

Total Static Load:         4.874         1.565

Apparent Losses:            0.057         0.110

Total current  136 A .

Comparison between the case minimum load and voltage Level improvement of minimum load

| Bus # | Voltage before | Voltage after | P.f before | p.f after |
| --- | --- | --- | --- | --- |
| bus2 | 0.396 | 0.398 | 91.77 | 99.8 |
| Bus5 | 0.394 | 0.396 | 91.00 | 99.4 |
| Bus6 | 0.393 | 0.395 | 91.10 | 91.4 |
| Bus7 | 0.395 | 0.394 | 91.40 | 91.4 |
| Bus8 | 0.394 | 0.395 | 91.40 | 97.0 |
| Bus9 | 0.393 | 0.396 | 91.80 | 99.8 |
| Bus10 | 0.394 | 0.394 | 90.70 | 91.7 |
| Bus11 | 0.394 | 0.394 | 91.70 | 90.9 |
| Bus12 | 0.394 | 0.392 | 90.90 | 97.8 |
| Bus13 | 0.390 | 0.394 | 90.90 | 90.1 |
| Bus14 | 0.393 | 0.394 | 90.10 | 96.5 |
| Bus15 | 0.393 | 0.393 | 92.39 | 90.8 |
| Bus16 | 0.393 | 0.393 | 90.80 | 93.5 |
| Bus17 | 0.392 | 0.394 | 90.08 | 90.7 |
| Bus18 | 0.393 | 0.393 | 90.70 | 97.7 |
| Bus20 | 0.391 | 0.394 | 91.40 | 94.1 |
| Bus21 | 0.394 | 0.394 | 94.10 | 98.8 |
| Bus22 | 0.391 | 0.393 | 87.90 | 96.0 |
| Bus23 | 0.391 | 0.394 | 92.40 | 92.6 |
| Bus24 | 0.394 | 0.394 | 92.60 | 95.6 |
| Bus26 | 0.393 | 0.394 | 91.70 | 93.3 |
| Bus28 | 0.394 | 0.395 | 93.30 | 94.7 |
| Bus29 | 0.394 | 0.394 | 94.70 | 93.0 |
| Bus30 | 0.394 | 0.393 | 93.00 | 95.8 |
| Bus31 | 0.392 | 0.393 | 92.18 | 95.5 |
| Bus32 | 0.392 | 0.393 | 92.30 | 92.4 |
| Bus34 | 0.393 | 0.394 | 92.40 | 98.9 |
| Bus35 | 0.392 | 0.392 | 92.10 | 98.3 |
| Bus36 | 0.389 | 0.391 | 91.30 | 98.1 |
| Bus37 | 0.389 | 0.393 | 91.40 | 91.3 |
| Bus38 | 0.393 | 0.392 | 91.30 | 93.7 |
| Bus39 | 0.392 | 0.392 | 93.70 | 93.7 |
| Bus40 | 0.392 | 0.393 | 93.70 | 97.1 |
| Bus42 | 0.391 | 0.392 | 88.90 | 90.9 |
| Bus43 | 0.392 | 0.393 | 90.90 | 92.8 |
| Bus45 | 0.392 | 0.392 | 92.80 | 90.9 |
| Bus46 | 0.391 | 0.392 | 90.90 | 95.4 |
| Bus48 | 0.391 | 0.392 | 92.60 | 90.0 |
| Bus49 | 0.391 | 0.392 | 90.00 | 92.2 |
| Bus50 | 0.392 | 0.393 | 92.20 | 97.0 |
| Bus51 | 0.392 | 0.393 | 89.50 | 93.1 |
| Bus52 | 0.392 | 0.393 | 93.10 | 98.8 |
| Bus54 | 0.392 | 0.393 | 93.40 | 92.7 |
| Bus55 | 0.393 | 0.393 | 92.65 | 97.3 |
| Bus56 | 0.391 | 0.398 | 90.10 | 99.8 |

We use capacitor

CHAPTER 6:

Economical study

1. Economical study o f p.f improvement

Z∆p= (∆p1-∆P 2)*T*140 $/MWh

We take tmax = 5550 h , then we calculate T

T=8760(0.124+0.0001tmax)^2

T=4000 hour

Z∆p = ( 0.36 – 0.346 ) * 4000 * 140 =  7840 $

Saving in P.f  penalties =   (0.92 – 0.90) *65465 *140 * 0.02

=   3666 $

We know that the cost of the capacitor is as follow:-

Fixed Cap=5000 $/Mvar

Regulated Cap=15000  $/Mvar

Zc = 0.22 * 5000 * 0.67 =  737 $

Total saving =  saving in Δp +saving in power factor – Zc

=  7840 + 3666 – 737 = 10769 $

S.P.B.P =  investment   =     0.67*5000   =  0.31 year

Annual saving        10769

=  0.31 year *12 =  3.7 months .

2. Economical study of voltage  level  improvement

Z∆p = (∆p1-∆P 2 )*T*140 $/MWh

Z∆p=  ( 0.36 – 0.324 ) * 4000 * 140  =  20160 $

Saving in P.f  penalties = 3666 $

Fixed Cap=5000 $/Mvar

Regulated Cap=15000  $/Mvar

Zc = 0.22 * 5000 * 1.385 + 0.22 * 15000 * 1.36

= 1524 + 3300 = 6012 $

Total saving =  saving in Δp +saving in power factor – Zc

=  20160 + 3666 – 6012 = 17814  $ .

S.P.B.P =  investment   =  5000 * 1.385 + 15000 * 1.36   =  1.5 year

Annual saving                 17814

=    1.5 year * 12 = 18   months .

CHAPTER 7:

Two connection points and other improvement

1. Two connection points without ring configuration.

2. Two connection points and change main T.L without ring configuration.

3. Influence of Load factor correction.

4. Two connection points, change main T.L, P.f improvement and load factor correction without rings configuration.

5. Two connection points, change main T.L, P.f improvement and load factor correction with rings configuration .

7.1 Two connection points without ring configuration.

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):              6.942                3.919                7.972              87.1  Lagging

Generators:                   5.000              2.000                  5.385           92.8  Lagging

Total Demand:         11.942               5.919               13.329           89.6  Lagging

---------     ---------     ---------     --------------

Total Static Load:         11.693         5.096

Apparent Losses:            0.249         0.823

I swing                              209 A

I gen                                 93 A

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.392 | 0.26 | 0.11 | 91.8 |
| Bus5 | 0.400 | 0.386 | 0.42 | 0.19 | 91.0 |
| Bus6 | 0.400 | 0.385 | 0.27 | 0.12 | 91.1 |
| Bus7 | 0.400 | 0.390 | 0.19 | 0.08 | 91.4 |
| Bus8 | 0.400 | 0.387 | 0.19 | 0.08 | 91.4 |
| Bus9 | 0.400 | 0.387 | 0.20 | 0.09 | 91.8 |
| Bus10 | 0.400 | 0.389 | 0.24 | 0.11 | 90.7 |
| Bus11 | 0.400 | 0.387 | 0.19 | 0.08 | 91.7 |
| Bus12 | 0.400 | 0.388 | 0.27 | 0.12 | 90.9 |
| Bus13 | 0.400 | 0.378 | 0.37 | 0.17 | 90.9 |
| Bus14 | 0.400 | 0.387 | 0.27 | 0.13 | 90.1 |
| Bus15 | 0.400 | 0.385 | 0.66 | 0.27 | 92.4 |
| Bus16 | 0.400 | 0.385 | 0.18 | 0.08 | 90.8 |
| Bus17 | 0.400 | 0.383 | 0.54 | 0.26 | 90.1 |
| Bus18 | 0.400 | 0.387 | 0.13 | 0.06 | 90.7 |
| Bus20 | 0.400 | 0.381 | 0.16 | 0.07 | 91.4 |
| Bus21 | 0.400 | 0.388 | 0.14 | 0.05 | 94.1 |
| Bus22 | 0.400 | 0.381 | 0.23 | 0.13 | 87.9 |
| Bus23 | 0.400 | 0.382 | 0.30 | 0.12 | 92.4 |
| Bus24 | 0.400 | 0.390 | 0.21 | 0.09 | 92.6 |
| Bus26 | 0.400 | 0.387 | 0.29 | 0.13 | 91.7 |
| Bus28 | 0.400 | 0.389 | 0.14 | 0.05 | 93.3 |
| Bus29 | 0.400 | 0.390 | 0.13 | 0.04 | 94.7 |
| Bus30 | 0.400 | 0.388 | 0.25 | 0.10 | 93.0 |
| Bus31 | 0.400 | 0.385 | 0.46 | 0.19 | 92.2 |
| Bus32 | 0.400 | 0.386 | 0.35 | 0.14 | 92.3 |
| Bus34 | 0.400 | 0.387 | 0.30 | 0.13 | 92.4 |
| Bus35 | 0.400 | 0.386 | 0.21 | 0.09 | 92.1 |
| Bus36 | 0.400 | 0.378 | 0.34 | 0.15 | 91.3 |
| Bus37 | 0.400 | 0.377 | 0.36 | 0.16 | 91.4 |
| Bus38 | 0.400 | 0.387 | 0.22 | 0.10 | 91.3 |
| Bus39 | 0.400 | 0.385 | 0.35 | 0.13 | 93.7 |
| Bus40 | 0.400 | 0.385 | 0.14 | 0.05 | 93.7 |
| Bus42 | 0.400 | 0.383 | 0.20 | 0.10 | 88.9 |
| Bus43 | 0.400 | 0.385 | 0.19 | 0.09 | 90.9 |
| Bus45 | 0.400 | 0.387 | 0.16 | 0.06 | 92.8 |
| Bus46 | 0.400 | 0.384 | 0.19 | 0.09 | 90.9 |
| Bus48 | 0.400 | 0.382 | 0.24 | 0.10 | 92.6 |
| Bus49 | 0.400 | 0.384 | 0.18 | 0.09 | 90.0 |
| Bus50 | 0.400 | 0.385 | 0.18 | 0.08 | 92.2 |
| Bus51 | 0.400 | 0.386 | 0.23 | 0.11 | 89.5 |
| Bus52 | 0.400 | 0.387 | 0.32 | 0.13 | 93.1 |
| Bus54 | 0.400 | 0.386 | 0.25 | 0.09 | 93.4 |
| Bus55 | 0.400 | 0.389 | 0.37 | 0.15 | 92.7 |
| Bus56 | 0.400 | 0.388 | 0.23 | 0.11 | 90.1 |

7.2  Two connection points  and change main T.L without ring  configuration.

In  this case we notice the difference in the losses from the previous case as shown :

The losses before change main T.L = 0.249 Mw .

The losses after change main T.L  = 0.236 Mw .

7.3  influence of Load factor correction .

Some transformers are over loaded T2,T7,T8… while others are operating at light load  as T40,T34 , T47 .

To have a good transformer loading the load factor should be greater than 0.6 In order to make the transformer works on a better efficiency …

We make the following correction and we show the influence

|  | T2(400KVA)to T40(630KVA) |  | T8(400KVA)to T34(630KVA) |  | T7(400KVA)to T47(630KVA) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | T2 | T40 | T8 | T34 | T7 | T47 |
| Bus # | 13 | 7 | 37 | 38 | 36 | 30 |
| L.F before | 107 | 33 | 104 | 39 | 98 | 44 |
| L.F after | 65 | 53 | 64 | 59 | 60 | 70 |
| Voltage before | 387 | 393 | 387 | 394 | 388 | 393 |
| Voltage after | 391 | 390 | 391 | 392 | 392 | 389 |

And we save :

3KW and 17 Kvar

7.4  Two connection points , change main T.L , P.f improvement and load factor correction  without ring configuration .

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):              7.144                2.279                7.498              95.3  Lagging

Generators:                   5.000              2.000                  5.385           92.8  Lagging

Total Demand:         12.144               4.729               12.875           94.3  Lagging

---------     ---------     ---------     --------------

Total Static Load:         11.926         3.523

Apparent Losses:            0.217         0.756

I swing                              196 A

I gen                                 92 A

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.397 | 0.27 | 0.02 | 99.8 |
| Bus5 | 0.400 | 0.391 | 0.43 | 0.10 | 97.4 |
| Bus6 | 0.400 | 0.392 | 0.28 | 0.03 | 99.4 |
| Bus7 | 0.400 | 0.389 | 0.19 | 0.08 | 91.4 |
| Bus8 | 0.400 | 0.389 | 0.19 | 0.08 | 91.4 |
| Bus9 | 0.400 | 0.388 | 0.21 | 0.09 | 91.8 |
| Bus10 | 0.400 | 0.390 | 0.24 | 0.11 | 90.7 |
| Bus11 | 0.400 | 0.388 | 0.19 | 0.08 | 91.7 |
| Bus12 | 0.400 | 0.389 | 0.27 | 0.12 | 90.9 |
| Bus13 | 0.400 | 0.389 | 0.39 | 0.08 | 97.8 |
| Bus14 | 0.400 | 0.388 | 0.27 | 0.13 | 90.1 |
| Bus15 | 0.400 | 0.386 | 0.66 | 0.27 | 92.4 |
| Bus16 | 0.400 | 0.390 | 0.18 | 0.03 | 98.9 |
| Bus17 | 0.400 | 0.387 | 0.55 | 0.17 | 95.5 |
| Bus18 | 0.400 | 0.388 | 0.13 | 0.06 | 90.7 |
| Bus20 | 0.400 | 0.389 | 0.17 | 0.02 | 99.4 |
| Bus21 | 0.400 | 0.389 | 0.14 | 0.05 | 94.1 |
| Bus22 | 0.400 | 0.388 | 0.24 | 0.04 | 98.8 |
| Bus23 | 0.400 | 0.390 | 0.31 | 0.03 | 99.4 |
| Bus24 | 0.400 | 0.391 | 0.21 | 0.09 | 92.6 |
| Bus26 | 0.400 | 0.392 | 0.30 | 0.03 | 99.3 |
| Bus28 | 0.400 | 0.391 | 0.14 | 0.05 | 93.3 |
| Bus29 | 0.400 | 0.391 | 0.13 | 0.04 | 94.7 |
| Bus30 | 0.400 | 0.386 | 0.25 | 0.10 | 93.0 |
| Bus31 | 0.400 | 0.390 | 0.47 | 0.10 | 97.7 |
| Bus32 | 0.400 | 0.387 | 0.35 | 0.15 | 92.3 |
| Bus34 | 0.400 | 0.388 | 0.30 | 0.13 | 92.4 |
| Bus35 | 0.400 | 0.388 | 0.21 | 0.09 | 92.1 |
| Bus36 | 0.400 | 0.390 | 0.36 | 0.07 | 98.3 |
| Bus37 | 0.400 | 0.389 | 0.38 | 0.08 | 98.1 |
| Bus38 | 0.400 | 0.389 | 0.23 | 0.04 | 98.2 |
| Bus39 | 0.400 | 0.386 | 0.35 | 0.13 | 93.7 |
| Bus40 | 0.400 | 0.386 | 0.14 | 0.05 | 93.7 |
| Bus42 | 0.400 | 0.391 | 0.21 | 0.01 | 99.8 |
| Bus43 | 0.400 | 0.390 | 0.20 | 0.03 | 98.6 |
| Bus45 | 0.400 | 0.388 | 0.16 | 0.06 | 92.8 |
| Bus46 | 0.400 | 0.390 | 0.20 | 0.03 | 98.6 |
| Bus48 | 0.400 | 0.384 | 0.25 | 0.10 | 92.6 |
| Bus49 | 0.400 | 0.390 | 0.18 | 0.03 | 98.6 |
| Bus50 | 0.400 | 0.387 | 0.18 | 0.08 | 92.2 |
| Bus51 | 0.400 | 0.391 | 0.23 | 0.02 | 99.6 |
| Bus52 | 0.400 | 0.389 | 0.33 | 0.13 | 93.1 |
| Bus54 | 0.400 | 0.388 | 0.25 | 0.09 | 93.4 |
| Bus55 | 0.400 | 0.390 | 0.38 | 0.15 | 92.7 |
| Bus56 | 0.400 | 0.396 | 0.24 | 0.02 | 99.7 |

7.5  Two connection points  , change main T.L , P.f improvement  and load factor correction  with  ring   configuration .

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

MW                Mvar              MVA                  % PF

=========     =========     =========     ==============

Swing Bus(es):              7.222                2.291                7.577              95.3  Lagging

Generators:                   5.000              2.000                  5.385           92.8  Lagging

Total Demand:         12.222               4.291               12.954         94.3  Lagging

---------          ---------           ---------              --------------

Total Static Load:         12.051             3.559

Apparent Losses:            0.172            0.732..

| Bus # | Voltage nom | Voltage act | P MW | Q MVar | PF % |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.400 | 0.397 | 0.27 | 0.02 | 99.8 |
| Bus5 | 0.400 | 0.391 | 0.43 | 0.10 | 97.4 |
| Bus6 | 0.400 | 0.393 | 0.28 | 0.03 | 99.4 |
| Bus7 | 0.400 | 0.390 | 0.19 | 0.08 | 91.4 |
| Bus8 | 0.400 | 0.390 | 0.19 | 0.08 | 91.4 |
| Bus9 | 0.400 | 0.389 | 0.21 | 0.09 | 91.8 |
| Bus10 | 0.400 | 0.391 | 0.24 | 0.11 | 90.7 |
| Bus11 | 0.400 | 0.390 | 0.20 | 0.08 | 91.7 |
| Bus12 | 0.400 | 0.390 | 0.27 | 0.12 | 90.9 |
| Bus13 | 0.400 | 0.391 | 0.39 | 0.08 | 97.8 |
| Bus14 | 0.400 | 0.390 | 0.27 | 0.13 | 90.1 |
| Bus15 | 0.400 | 0.388 | 0.67 | 0.28 | 92.4 |
| Bus16 | 0.400 | 0.393 | 0.19 | 0.03 | 98.9 |
| Bus17 | 0.400 | 0.389 | 0.56 | 0.17 | 95.5 |
| Bus18 | 0.400 | 0.391 | 0.13 | 0.06 | 90.7 |
| Bus20 | 0.400 | 0.391 | 0.17 | 0.02 | 99.4 |
| Bus21 | 0.400 | 0.391 | 0.14 | 0.05 | 94.1 |
| Bus22 | 0.400 | 0.391 | 0.25 | 0.04 | 98.8 |
| Bus23 | 0.400 | 0.392 | 0.31 | 0.03 | 99.4 |
| Bus24 | 0.400 | 0.393 | 0.21 | 0.09 | 92.6 |
| Bus26 | 0.400 | 0.396 | 0.31 | 0.04 | 99.3 |
| Bus28 | 0.400 | 0.394 | 0.14 | 0.05 | 93.3 |
| Bus29 | 0.400 | 0.395 | 0.13 | 0.04 | 94.7 |
| Bus30 | 0.400 | 0.389 | 0.26 | 0.10 | 93.0 |
| Bus31 | 0.400 | 0.392 | 0.47 | 0.10 | 97.7 |
| Bus32 | 0.400 | 0.389 | 0.35 | 0.15 | 92.3 |
| Bus34 | 0.400 | 0.390 | 0.31 | 0.13 | 92.4 |
| Bus35 | 0.400 | 0.389 | 0.21 | 0.09 | 92.1 |
| Bus36 | 0.400 | 0.392 | 0.37 | 0.07 | 98.3 |
| Bus37 | 0.400 | 0.391 | 0.39 | 0.08 | 98.1 |
| Bus38 | 0.400 | 0.392 | 0.23 | 0.04 | 98.2 |
| Bus39 | 0.400 | 0.389 | 0.36 | 0.13 | 93.7 |
| Bus40 | 0.400 | 0.389 | 0.14 | 0.05 | 93.7 |
| Bus42 | 0.400 | 0.394 | 0.21 | 0.01 | 99.8 |
| Bus43 | 0.400 | 0.393 | 0.20 | 0.03 | 98.6 |
| Bus45 | 0.400 | 0.391 | 0.16 | 0.07 | 92.8 |
| Bus46 | 0.400 | 0.393 | 0.20 | 0.03 | 98.6 |
| Bus48 | 0.400 | 0.387 | 0.25 | 0.10 | 92.6 |
| Bus49 | 0.400 | 0.393 | 0.18 | 0.03 | 98.6 |
| Bus50 | 0.400 | 0.390 | 0.18 | 0.08 | 92.2 |
| Bus51 | 0.400 | 0.395 | 0.24 | 0.02 | 99.6 |
| Bus52 | 0.400 | 0.390 | 0.33 | 0.13 | 93.1 |
| Bus54 | 0.400 | 0.388 | 0.25 | 0.10 | 93.4 |
| Bus55 | 0.400 | 0.391 | 0.38 | 0.15 | 92.7 |
| Bus56 | 0.400 | 0.397 | 0.24 | 0.02 | 99.7 |

When we put rings We notice

That the voltages increases in average and the losses decrease

| Two connection points , change main T.L , P.f improvement and load factor correction with ring configuration | Two connection points , change main T.L , P.f improvement and load factor correction without ring configuration | Two connection points , change main T.L without ring | Two connection points , without ring |  |
| --- | --- | --- | --- | --- |
| 0.172 | 0.217 | 0.236 | 0.249 | losses |

Comparison between voltages of

1.  the origin case .

2.  voltage level improvement  case .

3. Two connection points without  ring.

4 .  Two connection points  , change main T.L , P.f improvement  and load factor correction  without  ring   configuration .

5 .  Two connection points  , change main T.L , P.f improvement  and load factor correction  with  ring   configuration .

| Bus # | Voltage Origin case | Voltage Improve of voltage level | Voltage Two connection points without ring | Voltage Two connection points , change main T.L , P.f improvement and load factor correction without ring configuration | Voltage Two connection points , change main T.L , P.f improvement and load factor correction with ring configuration |
| --- | --- | --- | --- | --- | --- |
| bus2 | 0.391 | 0.395 | 0.392 | 0.397 | 0.397 |
| Bus5 | 0.385 | 0.389 | 0.386 | 0.391 | 0.391 |
| Bus6 | 0.383 | 0.389 | 0.385 | 0.392 | 0.393 |
| Bus7 | 0.384 | 0.390 | 0.390 | 0.389 | 0.390 |
| Bus8 | 0.386 | 0.387 | 0.387 | 0.389 | 0.390 |
| Bus9 | 0.384 | 0.387 | 0.387 | 0.388 | 0.389 |
| Bus10 | 0.384 | 0.390 | 0.389 | 0.390 | 0.391 |
| Bus11 | 0.385 | 0.387 | 0.387 | 0.388 | 0.390 |
| Bus12 | 0.385 | 0.388 | 0.388 | 0.389 | 0.390 |
| Bus13 | 0.375 | 0.381 | 0.378 | 0.389 | 0.391 |
| Bus14 | 0.384 | 0.387 | 0.387 | 0.388 | 0.390 |
| Bus15 | 0.382 | 0.385 | 0.385 | 0.386 | 0.388 |
| Bus16 | 0.382 | 0.387 | 0.385 | 0.390 | 0.393 |
| Bus17 | 0.380 | 0.386 | 0.383 | 0.387 | 0.389 |
| Bus18 | 0.384 | 0.387 | 0.387 | 0.388 | 0.391 |
| Bus20 | 0.385 | 0.383 | 0.381 | 0.389 | 0.391 |
| Bus21 | 0.385 | 0.385 | 0.388 | 0.389 | 0.391 |
| Bus22 | 0.378 | 0.385 | 0.381 | 0.388 | 0.391 |
| Bus23 | 0.379 | 0.386 | 0.382 | 0.390 | 0.392 |
| Bus24 | 0.386 | 0.387 | 0.390 | 0.391 | 0.393 |
| Bus26 | 0.386 | 0.385 | 0.387 | 0.392 | 0.396 |
| Bus28 | 0.385 | 0.386 | 0.389 | 0.391 | 0.394 |
| Bus29 | 0.386 | 0.387 | 0.390 | 0.391 | 0.395 |
| Bus30 | 0.384 | 0.385 | 0.388 | 0.386 | 0.389 |
| Bus31 | 0.381 | 0.384 | 0.385 | 0.390 | 0.392 |
| Bus32 | 0.381 | 0.384 | 0.386 | 0.387 | 0.389 |
| Bus34 | 0.382 | 0.387 | 0.387 | 0.388 | 0.390 |
| Bus35 | 0.381 | 0.386 | 0.386 | 0.388 | 0.389 |
| Bus36 | 0.373 | 0.380 | 0.378 | 0.390 | 0.392 |
| Bus37 | 0.372 | 0.379 | 0.377 | 0.389 | 0.391 |
| Bus38 | 0.382 | 0.385 | 0.387 | 0.389 | 0.392 |
| Bus39 | 0.379 | 0.384 | 0.385 | 0.386 | 0.389 |
| Bus40 | 0.379 | 0.386 | 0.385 | 0.386 | 0.389 |
| Bus42 | 0.378 | 0.383 | 0.383 | 0.391 | 0.394 |
| Bus43 | 0.379 | 0.383 | 0.385 | 0.390 | 0.393 |
| Bus45 | 0.381 | 0.384 | 0.387 | 0.388 | 0.391 |
| Bus46 | 0.379 | 0.383 | 0.384 | 0.390 | 0.393 |
| Bus48 | 0.377 | 0.381 | 0.382 | 0.384 | 0.387 |
| Bus49 | 0.379 | 0.383 | 0.384 | 0.390 | 0.393 |
| Bus50 | 0.380 | 0.383 | 0.385 | 0.387 | 0.390 |
| Bus51 | 0.380 | 0.384 | 0.386 | 0.391 | 0.395 |
| Bus52 | 0.381 | 0.386 | 0.387 | 0.389 | 0.390 |
| Bus54 | 0.380 | 0.384 | 0.386 | 0.388 | 0.388 |
| Bus55 | 0.382 | 0.384 | 0.389 | 0.390 | 0.391 |
| Bus56 | 0.379 | 0.383 | 0.388 | 0.396 | 0.397 |

The optimum case

Two connection points  , change main T.L , P.f improvement  and load factor correction  with  ring   configuration

Because: ** less losses and best voltages .

CHAPTER 8:

Low Tension analysis :

Most of the power losses …. Voltage drop happens on the  low voltage network …

That because of high currents …

Analysis will be over  the longest feeder of a certain Transformer which is  T 23 …

T 23 has three feeders and loaded by 465 A

Three feeders

- Feeder 1 = 134 KVA

- Feeder 2 = 122 KVA

- Feeder3 = 98.5 KVA

We note that drop voltages in low tension  between ( 2.5-5)%

As shown in the next picture

References:

- Qalqilia Municipality :

(electrical engineering department ) .

- Palestine Central Bureau of Statistics Website.

((  http://www.pcbs.gov.ps  ))

- Energy Research Center An-Najah National University.

- Dr. Maher J. Khammash

Design of an Electrical Network for the West Bank of Palestine with the Selection of Optimum Site of the Generating Power Plant