## Slide 1: An-Najah National University Civil Engineering Department Graduation project Hydraulic analysis & Redesign of Al-Masaken & Old Askar Camp Water Supply Network Submitted by: Leen Masri Duaa Dweikat Supervisor: Dr. Anan Jayossi 2012

## Slide 2: project main objectives
This project aims to analyze the water distribution
network of Al–Masaken and Old Askar Camp Area .
Modify or redesign the network in order to meet
the area citizens' water requirements in accordance
with population growth until 2040.

## Slide 3: Study Area
Al-Masaken AlShaabeya and Old Askar Camp are
located in the eastern part of Nablus city.
It’s population is about 25082 persons.
It’s area is about 884.534 donums.
It’s supplied with water directly from Al-Baddan
well.

## Slide 4: Questionnaire analysis
Questionnaires covers 42 families which were
chosen randomly.
It was divided into two categories:
General information about the inhabitants.
Information about water network

## Slide 5: The Questionnaire (cont’)
Chart: Family income (NIS)
| <1000 | 1000-2000 | 2000-3000 | >4000
 | 4 | 14 | 16 | 42
The figure below shows the relationship between the family income and average consumption.

## Slide 6: The Questionnaire (Cont.)
Chart: Water quality
| Good | moderate | bad
 | 28 | 11 | 3
The figure below shows that houses that have gardens consume water more than the houses that don’t have ones.
Most of people don’t complain of water quality in Al-Masaken El-Sha’abya and Old Askar Camp as shown in the figure below.
Chart: water consumption - garden presence relationship
| have garden | don't have garden
 | 14.47 | 12.64

## Slide 7: EPANET
EPANET program is one of the networks modeling software that performs extended period simulation of hydraulic and water quality behavior within pressurized pipe networks.
The program tracks the flow of water in each pipe ,the pressure at each node, the height at water in each
tank or reservoir.

## Slide 8: EPANET Network

## Slide 9: Existing water network description
The Existing water network has 121 pipes with different diameters (2, 3, 4, 6, 8, 10, 12) inch of Polyethylene and polypropylene pipe.
It has 93 nodes with different elevations.
Existing water network gets water directly from Al-Badan Well through the main link which has a pressure of 7.5 bar.
It has a continuous rate of pumping .

## Slide 10: EPANET- Input Data
A group of tables were prepared to be used in
EPANET program to simulate the network.
Here are samples of this tables:
This table represent nodes characteristic:
Node number | Elevation(m)
1 | 499.5
2 | 506.3
3 | 520
4 | 507.7
5 | 511
6 | 515
7 | 519

## Slide 11: EPANET –Input Data (cont.)
Pipe ID | from | to | Length (m) | Diameter (in) | C
1 | Tank | 1 | 10 | 16 | 140
101 | 1 | 2 | 51 | 12 | 140
102 | 2 | 3 | 315 | 4 | 140
103 | 2 | 4 | 64 | 10 | 140
104 | 4 | 5 | 78 | 10 | 140
105 | 5 | 6 | 148 | 8 | 140
Pipe characteristic table:

## Slide 12: EPANET-Input Data (Cont.)
Node number | Area served by each node | Total Area (m²) | Population | Demand (L/d)
1 | A7 /10 + A10 /7 | 7860.31 | 223 | 23660.3
2 | A7 /10+ A10 /7+A18 /4 | 14207.91 | 403 | 42758.3
3 | A18 /4 | 6347.6 | 180 | 19098
4 | A10 /7 | 4565.85 | 129 | 13686.9
5 | A10 /7 | 4565.85 | 129 | 13686.9
6 | A10 /7+A11 /7 | 13166.35 | 373 | 39575.3
Demand for each node table:
Assuming that our study area has a uniform density which equal to .02835 c/m² according to this equation:
Density = Total population/ total area
The study area is divided into small areas and each node gets part of area that serves it. As show in the table.

## Slide 13: EPANET-Input Data
Population served by each node calculated from multiplying the Area served by that node by the Density.
Consumption per capita day is (75.23 L/c.d)
UFW% equals to 29.1%
Demand per capita days equal to 106.1 L/c.d
Using this equation :
Demand = consumption / (1- UFW%)
Node's demand was found by multiplying demand per capita-day by pop. served at each node

## Slide 14: EPANET - Output Data
the main elements of the EPANET output that have been used to analyze and redesign the network was the pressure at each node & the velocity in each pipe.
This project’s criteria was “20-70 m” pressure
“0.1-3 m/s” velocity

## Slide 15: EPANET-Output Data(cont.)
Node ID | Demand (LPS) | Head (m) | Pressure (m)
1 | 0.55 | 585.63 | 86.13
2 | 0.99 | 585.43 | 79.13
3 | 0.44 | 585.41 | 65.41
4 | 0.32 | 585.33 | 77.63
5 | 0.32 | 585.25 | 74.25
6 | 0.92 | 584.81 | 69.81
7 | 1.45 | 584.59 | 65.59
Link ID | Flow (LPS) | Velocity (m/s) | Unit head loss(m/km)
101 | 83.21 | 1.18 | 3.99
102 | 0.44 | 0.06 | 0.05
103 | 30.49 | 0.62 | 1.51
104 | 24.71 | 0.5 | 1.02
105 | 24.40 | 0.78 | 2.96
106 | 20.58 | 0.66 | 2.16
107 | 17.68 | 0.56 | 1.63
EPANET present Node results
EPANET present Link results

## Slide 16: EPANET Output (cont.)
Pressure of nodes : there is no negative pressure and all values are above 20 m.
Velocity of pipe :velocities range between (0.01-2) m/s this means that there are values less than 0.1m/s. Low values of velocity results from large pipe’s diameter and dead ends.

## Slide 17
Future water network

## Slide 18: Population forecast
The future population in 2040 is about 50000c according to this curve:
Population forecast
It can also be calculated based on this equation:
Pf=Pp (1+i)^n
The growth rate for ALMasaken is (3.2%)
And for Old Askar Camp is around zero (0.5%).

## Slide 19: Future Demand Estimation
Future consumption is 120 L/c.d. While Physical
losses is 15 % .
The future demand was considered to be 141 L/c.d
according to this equation:
demand = Future consumption / (1- physical losses)
To estimate the future water demand for each node, the
existing demand was multiplied by a factor that is
calculated as follows:
Factor = (population 2040/population 2010) * (demand
2040/demand 2010)
= 2.65
*

## Slide 20: EPANET - Input Data
Here ‘s a sample for the future demand calculation which will be used in EPANET ‘s future input value:
Node number | Demand 2010 (L/d) | demand 2040 (L/d)
1 | 23660.3 | 62699.8
2 | 42758.3 | 113309.5
3 | 19098 | 50609.7
4 | 13686.9 | 36270.3
5 | 13686.9 | 36270.3
6 | 39575.3 | 104874.5
Future demand for each node

## Slide 21: EPANET - Input Data
Due to continuous pumping the following pattern was used:
Demand Pattern

## Slide 22: EPANET-Output Data
Pressure of nodes : there is no negative pressure and all values are above 20 m.
Velocity of pipe : velocity values are within the range of (.01-4.17) m/s that means we should change diameter of the pipes in order to have velocities within the range of (.1-3) m/s

## Slide 23: Modification
Pipe ID | Old diameter(mm) | New diameter (mm)
1 | 300 | 400
101 | 300 | 400
112 | 250 | 300
128 | 250 | 300
144 | 200 | 250
146 | 100 | 150
147 | 100 | 150
211 | 200 | 300
218 | 75 | 100
Modification has been made to meet the future requirements :
Pipe diameter changes

## Slide 24: EPANET - Output Data
Node ID | Demand (LPS) | Head (m) | Pressure (m)
1 | 1.45 | 585.09 | 85.58
2 | 2.62 | 584.78 | 78.48
3 | 1.17 | 584.68 | 64.68
4 | 0.84 | 584.27 | 76.57
5 | 0.84 | 583.84 | 72.84
Node Results for the year 2040
Link ID | Flow (LPS) | Velocity (m/s) | Unit Headloss (m/km)
101 | 220.51 | 1.75 | 5.97
102 | 1.17 | 0.15 | 0.31
103 | 75.09 | 1.53 | 8.01
104 | 61.36 | 1.25 | 5.51
105 | 60.52 | 1.93 | 15.93
Link Results for the year 2040

## Slide 25: Cost
Here’s a sample of table that summarizes the cost
calculation for the pipes:
Cost calculations for the pipes
Pipe ID | Length (m) | Diameter (in) | Cost ($)/m | Cost ($)
1 | 10 | 16 | 140 | 1400
101 | 51 | 16 | 140 | 7140
102 | 315 | 4 | 53 | 16695
103 | 64 | 10 | 94 | 6016
104 | 78 | 10 | 94 | 7332
105 | 148 | 8 | 76 | 11248
106 | 105 | 8 | 76 | 7980
We can see that the approximate cost for the pipes only is about 783090 $.

## Slide 26
Thank you for your attention