## Slide 1: Selat al-daher water distribution network
Prepared By :
Mohammad Waleed Abu Diak
Anas Wasef Ali

## Slide 2
Objective
* Analyze and Redesign the existing
water distribution network in
Selat Al-Daher to be valid for
the next 30 years

## Slide 3
Project Description
* Site Selection
* Have a contour and water network maps
* Data Collection
* Analysis the existing water network
* Solve the problems

## Slide 4
Study Area
Selat Al-Daher
* Located 14 km south of Jenin
* Current population is 6900 capita
51% males and 49% females
* The Average height of the town is 400 m
* Surrounded by Al-Attara,
Al-Fandaqomia, Burqa And Bezarya

## Slide 5
Chart: 
| Dec | Nov | Oct | Sep | Aug | Jul | Jun | May | Apr | Mar | Feb | Jan
 | 88 | 60 | 13 | 0 | 0 | 0 | 0 | 5 | 17 | 52 | 95 | 123
Chart: 
| Dec | Nov | Oct | Sep | Aug | Jul | Jun | May | Apr | Mar | Feb | Jan
 | 14 | 19.4 | 23.5 | 26 | 27.6 | 27 | 25.6 | 23.2 | 18.3 | 14.6 | 12.8 | 12.4
Precipitation rates
Temperature rates

## Slide 6
Questionnaire Analysis
* Family Size is 7 persons per family
* Average daily consumption is 69 l/c/day
*Average daily demand is 106 l/c/day

## Slide 7
Chart: 
| University | Tawjihi | Less than Tawjihi
 | 0.38 | 0.42 | 0.2
Education

## Slide 8
Chart: 
| less than 1000 NIS | 1000-2000 NIS | 2000-3000 NIS | More than 3000 NIS
 | 0.02 | 0.14 | 0.48 | 0.36
Monthly Income

## Slide 9
Chart: 
| Both | Agriculture | Animal | Nothing
 | 0.08 | 0.54 | 0.08 | 0.3
Farms Percentage

## Slide 10
Existing Water Distribution
Network
* No As-Built plan for the network
* The source of water is Mekarot
* Losses in the network equal to 35 %
taken from minisipilaty

## Slide 14
Epanet Analysis for
Existing Network
* 6 main water supply pipes
Presented with two reservoirs
* Only one pump
* Demand pattern equal to 5
* Many Problems discovered

## Slide 15
Future Design
* Design Period is 30 years
* Growth Rate is 1.836%
* Population at 2041 is 11909 capita
* Population Equation is
* Steel Pipes used with 110 HW coefficient

## Slide 16
* Assumed value of consumption
is 120 l/c/day
* Physical Losses in the network is 15%
* Future Demand is 141 l/c/day
* Future demand factor is 2.294

## Slide 17
Design Constraints
* Velocity Limit 0.1 – 3 m/sec
* Pressure Limit 30 – 160 m

## Slide 18
Future Epanet Run
* Two Runs, Before and after
Redesign the network

## Slide 19
Before
After

## Slide 20
Before
After

## Slide 23
Results and recommendations
* Min Velocity is 0.18 m/sec
* Max velocity is 2.95 m/sec
* Min Pressure is 9.88 m
* Max pressure is 171.23 m
* PRV recommended to be used in two links

## Slide 24
Total Cost for each diameter size |  |  | 
Cost($) | Cost($/m) | Pipes length | Diameter
25004 | 28 | 893 | 2
78948 | 45 | 1754.4 | 3
91665.6 | 52 | 1762.8 | 4
59828.8 | 61 | 980.8 | 6
58603.6 | 76 | 771.1 | 8
314050 |  | 6162.1 | Total
Cost of the Project

## Slide 25: Thank you so much