Table Of Contents

| NO. | Content | Page |
| --- | --- | --- |
|  | Abstract | 2 |
|  | Energy sector in palestine | 3 |
|  | Information about tubas town | 3 |
|  | Introduction | 4 |
| Chapter one | Electrical Network | 5 |
| 1.1 | Electrical supply | 5 |
| 1.2 | Element of tubas network | 5-7 |
| 1.3 | Energy consumption | 7 |
| 1.3.1 | The nature of load & dialy load curve | 8 |
| 1.3.2 | The growth rate of the load | 9 |
| Chapter two | Analysis of the network | 10 |
| 2.1 | Etap power station | 10 |
| 2.2 | Data needed for the load flow analysis | 11-12 |
| 2.3 | maximum case | 12 |
| 2.3.1 | The medium & The low tension voltages | 12-14 |
| 2.3.2 | Value of max. loads(before improvement) | 15-17 |
| 2.3.3 | summary | 17 |
| 2.3.4 | Problems of the tubas electrical network | 18 |
| 2.4 | The maximum load improvement | 19 |
| 2.4.1 | Increasing the swing voltage | 19-21 |
| 2.4.2 | Improvement the voltage using tap changing | 21-23 |
| 2.4.3 | Power factor improvement | 23-27 |
| 2.4.4 | Voltage level improvement | 28-29 |
| 2.4.5 | Comparison between three case | 30-31 |
| Chapter three | Minimum case | 32 |
| 3.1 | Value of min. loads(before improvement) | 32-34 |
| 3.1.1 | The medium & The low tension voltages | 34-35 |
| 3.1.2 | summary | 36 |
| 3.2 | The minimum load improvement | 36 |
| 3.2.1 | The min. load after improvrment using tap | 36-38 |
| 3.2.2 | Power factor improvement | 38-41 |
| 3.2.3 | Comparison between three case | 41-43 |
| 3.2.4 | Voltage level improvement | 44-46 |
| Chapter four | Two connection point | 47-49 |
| Chapter five | Economical study | 50- |

Abstract

Our project is to make a load flow study and analysis for TUBAS Electrical Network using ETAP software to improve the power factor and to reduce the electrical losses in the network and so, reducing the penalties in the total tariff  for the municipality, increasing the reliability of the network. More over we want to increase the capability of the transformers and the transmission lines

Load flow analysis

In power system analysis The Load Flow study is a basic and commonly needed electrical study. The Load Flow study will show the power in KVA or Amperes that is being handled by all of the individual electrical components, e.g. transformers, conductors and panels in the system. This allows a determination of equipment rating margins and reserve capacity loading percentage.Analysis and study of distribution electrical networks may cover conventional voltage drop analysis, power losses analysis, power factor considerations, capacitors’ placements (correction of power factor).

Prospective goals of the study :-

1. Reduction of power losses

2. Increasing of voltage levels

3. Reducing the penalties by improving  the P.F.

4. Increasing the capability of the transformers.

5. Increasing the reliability of the network .

Methods of improvement of operating condition in electrical networks :-

1. Swing bus control

2. Transformer taps

3. Installation of capacitor banks (reactive power compensation)

4. Changing the configuration of distribution network (radial              ring)

Energy sector in Palestine

Energy sector in Palestine faced sever since the Israeli occupation , financial and management obstacles due to the severe restrictions imposed by the Israeli occupation. as a result of this situation Palestine has not yet a unified power system , the existing network is local low voltage distributions networks connected to Israeli electrical corporation (IEC) , where around 97% of consumed energy were and still supplied by the IEC .The voltages of the existing distribution networks are : ( 0.4 , 6.6 , 11 , 22 , and 33 KV ) .  IEC supplies electricity to the electrified communities by 22 or 33 KV by overhead lines . electricity is purchased from IEC and then distributed to the consumers. The existing electricity situation is characterized in old fashion over loaded networks , high power losses ( more than 20% ) , low power factor ,poor system reliability , high prices of electricity supplied to the consumer due to high tariff determined by the IEC in addition , many villages depend on diesel generators to provide their own needs of electrical energy .Due to all factors mentioned above, it becomes very important to design a national independent power system for the west bank of Palestine which will connect all the west bank areas by a reliable network to a national generating plant . the national power system should have the minimum annual cost and provide the consumer with a high quality of electric energy . this power system should also reduced the cost of KWH and be able to provide electricity to any area in the west bank .

Information about Tubas town :

TUBAS is a Palestinian city which is located in the north eastern part of the West Bank. Thecity is located to the west of the Governorate of Tubas. It is bordered by Tayasir and Alaqaba villages to the east, Aqqaba to the north, Aljadedah and Sereas villages (Jenin Governorate) to the west and Tamun and Alfarha to the south

The total area of Tubas city is 295,123 dunums, which represents approximately 55.6 % of theTubas Governorate's land area. 3000 dunums are classified as 'built up' areas, whilst 150,000dunums are agricultural, and 180,000 further dunums have been confiscated by Israelioccupation.Tubas city is the administrative center of the Governorate of Tubas and also the largestlocality. Whereas most of the governorate is in the Jordan valley, Tubas itself is located in thehills of the West Bank at the moderate elevation of 362 m above sea level.

Introduction

The power system in general consist of these parts:

- Generating station: And this part consists of

- Generators in which electric power is produced by 3-phase alternators operating in parallel. And usually electric power is generated at voltages of 12kv to 25kv.

- Sub-station, where the power transformers step up the voltage to between 66kv 1000kv.

- Primary transmission. The electric power at high voltages is transmitted by 3-phase 3-wire over head system to the outskirts of the city. This forms the primary transmission.

- Secondary transmission. The primary transmission line terminates at the receiving station which usually lies at the outskirts of the city. At the receiving station the voltage is reduced to 33kv or 22kv by step-down transformers.

- Primary distribution. the secondary transmission line terminates at the sub-station where voltage is reduced from the secondary voltage to the primary distribution voltage usually 11kv ,could be 6.6kv 3-phase 3-wire .the 11kv lines run along the important road sides of the city . And forms the primary distribution.

- Secondary distribution. The electric power form primary distribution line is delivered to distribution sub-stations. These sub-stations are located near the consumers localities and step down the voltage to 400v 3-phase 4-wire for secondary distribution. And this forms secondary distribution.

Chapter One:

  - Electrical supply

TUBAS ELECTRICAL NETWORK is provided by Israel electrical company(IEC) through an over head transmission line  of 33 kv.The main circuit breaker is rated at (200 A).the max demand is reached (10MVA).

The main supply for electrical distribution network  in the tyaseer. And the voltage of the existing distribution networks are 33 kv only.IEC supplies electricity to the electrified communities by 33 KV by overhead lines . Electricity is purchased from IEC and then distributed to the consumers.Palestine has not yet a unified power system , the existing network is local low voltage distributions networks connected to Israeli electrical corporation (IEC) , where around 97% of consumed energy were and still supplied by the IEC .

1.2 Element of Tubas network

In this section we will study the elements of the network such as transformers, over head lines and underground cables.

1.2.1  Distribution Transformers:

Tubas  network consists of  73 - Δ/Υ - ,  33/0.4 KV distribution transformers.

And the table shows the number of each of them and the rated KVA:

| Number of Transformers | Transformer Ratings (KVA) |
| --- | --- |
| 5 | 630 |
| 19 | 400 |
| 27 | 250 |
| 4 | 160 |
| 15 | 100 |
| 3 | 50 |

1.2.2 Medium voltage 33kv lines :

- Overhead lines:

The conducters used in the network are ACSR (120mm2 &  95mm2 & 50mm2)

The resistance and reactance of the ACSR conducter

In the table below:

| ACSR CABLE | R(Ohms/Km) | X(Ohms/Km) |
| --- | --- | --- |
| 120mm2 | 0.219 | 0.269 |
| 95mm2 | 0.301 | 0.322 |
| 50mm2 | 0.543 | 0.333 |

2.Under ground cable

The under ground cable used in the network are XLPE Cu (95mm2 & 120mm2).

The resistance and reactance of XLPE in table below

| XLPE CABLE | R(Ohms/Km) | X(Ohms/Km) |
| --- | --- | --- |
| 95mm2 | 0.41 | 0.121 |
| 120mm2 | 0.196 | 0.117 |

1.3 Energy consumption

In this section we will talk about the consumption of energy in Tubas  network:

1.3.1 The nature of the load

The table bellow shows the consumers classification and their size.

| 47% | Residential |
| --- | --- |
| 25% | Industrial |
| 13% | Commercial |
| 15% | Others |

- The daily load curve :

We take readings to the load changes during the day, the result gives the graph below :

The daily load curve  we have very important information like:

- Max demand

- Load factor

- The suitable distribution of the load

- Total energy consumption

- How to avoid penalties and other important things

1.3.2 The growth rate of the load

The table below shows the total consumption of energy for 5 years .

| Year | Average Monthly consumption In MWH | Percentage growth % |
| --- | --- | --- |
| 2006 | 20,000 | --------------- |
| 2007 | 30,000 | 50% |
| 2008 | 40,000 | 33% |
| 2009 | 50,000 | 25% |
| 2010 | 60,000 | 20% |

We notice that the energy purchased from the ICE is changing during the

Years.

Chapter Two:

Analysis Of The Network:

2.1  ETAP power station

ETAP PowerStation allows us to work directly with graphical one line diagram.

And it provides us with text reports such as:

1.complete report.

2.Input data.

3.Results .

4.Summary reports

2.2 Data needed for the load flow analysis:

2.2.1 power factor & load factor calculation

| Trans | S(rated) KVA | S(actual) KVA | LF | P.F | P(load) KW |
| --- | --- | --- | --- | --- | --- |
| 1 | 100 | 65 | 0.65 | 0.79 | 51.35 |
| 2 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 3 | 100 | 75 | 0.75 | 0.88 | 66 |
| 4 | 250 | 200 | 0.8 | 0.92 | 184 |
| 5 | 250 | 170 | 0.68 | 0.99 | 168.3 |
| 6 | 250 | 200 | 0.8 | 0.92 | 184 |
| 7 | 400 | 300 | 0.75 | 0.92 | 276 |
| 8 | 400 | 305 | 0.76 | 0.95 | 290 |
| 9 | 250 | 150 | 0.6 | 0.93 | 139.5 |
| 10 | 630 | 400 | 0.63 | 0.93 | 372 |
| 11 | 400 | 310 | 0.77 | 0.70 | 217 |
| 12 | 400 | 280 | 0.7 | 0.89 | 249.2 |
| 13 | 400 | 270 | 0.67 | 0.90 | 243 |
| 14 | 250 | 190 | 0.76 | 0.88 | 167.2 |
| 15 | 250 | 150 | 0.6 | 0.98 | 147 |
| 16 | 250 | 120 | 0.48 | 0.88 | 105.6 |
| 17 | 250 | 160 | 0.64 | 0.86 | 137.5 |
| 18 | 250 | 170 | 0.68 | 0.91 | 154.7 |
| 19 | 250 | 180 | 0.72 | 0.88 | 154 |
| 20 | 250 | 120 | 0.48 | 0.89 | 158.4 |
| 21 | 400 | 330 | 0.82 | 0.88 | 290.4 |
| 22 | 100 | 30 | 0.3 | 0.76 | 22.8 |
| 23 | 250 | 175 | 0.7 | 0.93 | 162.75 |
| 24 | 400 | 255 | 0.64 | 0.92 | 234.6 |
| 25 | 400 | 350 | 0.87 | 0.98 | 343 |
| 26 | 400 | 300 | 0.75 | 0.83 | 249 |
| 27 | 400 | 220 | 0.55 | 0.94 | 207 |
| 28 | 100 | 70 | 0.7 | 0.94 | 65.8 |
| 29 | 50 | 35 | 0.7 | 0.90 | 31.5 |
| 30 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 31 | 400 | 400 | 1.0 | 0.91 | 364 |
| 32 | 50 | 35 | 0.7 | 0.92 | 32.2 |
| 33 | 100 | 70 | 0.7 | 0.87 | 60.9 |
| 34 | 400 | 250 | 0.62 | 0.90 | 225 |
| 35 | 250 | 175 | 0.7 | 0.91 | 159.25 |
| 36 | 100 | 70 | 0.7 | 0.90 | 63 |
| 37 | 400 | 300 | 0.75 | 0.90 | 270 |
| 38 | 100 | 60 | 0.6 | 0.74 | 44.4 |
| 39 | 100 | 70 | 0.7 | 0.78 | 54.6 |
| 40 | 100 | 75 | 0.75 | 0.91 | 68 |
| 41 | 400 | 290 | 0.72 | 0.92 | 267 |
| 42 | 160 | 120 | 0.75 | 0.94 | 113 |
| 43 | 400 | 300 | 0.75 | 0.96 | 288 |
| 44 | 400 | 300 | 0.75 | 0.91 | 273 |
| 45 | 160 | 112 | 0.7 | 0.94 | 105.28 |
| 46 | 100 | 50 | 0.5 | 0.94 | 47 |
| 47 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 48 | 160 | 100 | 0.62 | 0.90 | 90 |
| 49 | 100 | 70 | 0.7 | 0.90 | 63 |
| 50 | 250 | 175 | 0.7 | 0.88 | 154 |
| 51 | 250 | 175 | 0.7 | 0.92 | 161 |
| 52 | 400 | 280 | 0.7 | 0.96 | 268.8 |
| 53 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 54 | 630 | 430 | 0.68 | 0.92 | 395.6 |
| 55 | 100 | 80 | 0.8 | 0.92 | 73.6 |
| 56 | 250 | 175 | 0.7 | 0.94 | 164.5 |
| 57 | 160 | 100 | 0.62 | 0.90 | 90 |
| 58 | 100 | 70 | 0.7 | 0.95 | 66.5 |
| 59 | 250 | 175 | 0.7 | 0.94 | 164.5 |
| 60 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 61 | 50 | 35 | 0.7 | 0.90 | 31.5 |
| 62 | 250 | 175 | 0.7 | 0.88 | 154 |
| 63 | 100 | 62 | 0.62 | 0.92 | 57 |
| 64 | 100 | 65 | 0.65 | 0.88 | 57.2 |
| 65 | 250 | 175 | 0.7 | 0.90 | 157.5 |
| 66 | 250 | 175 | 0.7 | 0.88 | 154 |
| 67 | 400 | 280 | 0.7 | 0.90 | 252 |
| 68 | 630 | 425 | 0.67 | 0.90 | 382.5 |
| 69 | 630 | 205 | 0.57 | 0.90 | 184.5 |
| 70 | 630 | 441 | 0.7 | 0.90 | 396.9 |
| 71 | 400 | 300 | 0.75 | 0.90 | 270 |
| 72 | 250 | 175 | 0.7 | 0.86 | 150.5 |
| 73 | 250 | 175 | 0.7 | 0.89 | 155.75 |

2.3 The maximum case

2.3.1 the medium voltages & The low tension voltages

The actual medium voltages and low voltage on each transformer is shown in the table below :

| Transformer number | Medium voltage(rated) Kv | Medium voltage(actual) kv | Low voltage(rated) kv | Low voltage(actual) kv |
| --- | --- | --- | --- | --- |
| 1 | 33 | 33 | 0.4 | 0.396 |
| 2 | 33 | 32.854 | 0.4 | 0.394 |
| 3 | 33 | 32.565 | 0.4 | 0.390 |
| 4 | 33 | 32.35 | 0.4 | 0.388 |
| 5 | 33 | 32.344 | 0.4 | 0.388 |
| 6 | 33 | 32.333 | 0.4 | 0.389 |
| 7 | 33 | 32.29 | 0.4 | 0.387 |
| 8 | 33 | 32.261 | 0.4 | 0.387 |
| 9 | 33 | 32.203 | 0.4 | 0.386 |
| 10 | 33 | 32.129 | 0.4 | 0.385 |
| 11 | 33 | 31.98 | 0.4 | 0.380 |
| 12 | 33 | 31.928 | 0.4 | 0.382 |
| 13 | 33 | 31.8 | 0.4 | 0.380 |
| 14 | 33 | 31.787 | 0.4 | 0.379 |
| 15 | 33 | 31.772 | 0.4 | 0.379 |
| 16 | 33 | 31.77 | 0.4 | 0.381 |
| 17 | 33 | 31.769 | 0.4 | 0.381 |
| 18 | 33 | 31.764 | 0.4 | 0.379 |
| 19 | 33 | 31.764 | 0.4 | 0.380 |
| 20 | 33 | 31.763 | 0.4 | 0.379 |
| 21 | 33 | 31.763 | 0.4 | 0.382 |
| 22 | 33 | 31.82 | 0.4 | 0.382 |
| 23 | 33 | 31.721 | 0.4 | 0.378 |
| 24 | 33 | 31.695 | 0.4 | 0.378 |
| 25 | 33 | 31.69 | 0.4 | 0.379 |
| 26 | 33 | 31.624 | 0.4 | 0.379 |
| 27 | 33 | 31.614 | 0.4 | 0.376 |
| 28 | 33 | 31.571 | 0.4 | 0.377 |
| 29 | 33 | 31.536 | 0.4 | 0.377 |
| 30 | 33 | 31.516 | 0.4 | 0.376 |
| 31 | 33 | 31.515 | 0.4 | 0.374 |
| 32 | 33 | 31.524 | 0.4 | 0.376 |
| 33 | 33 | 31.524 | 0.4 | 0.377 |
| 34 | 33 | 31.521 | 0.4 | 0.376 |
| 35 | 33 | 31.515 | 0.4 | 0.374 |
| 36 | 33 | 31.512 | 0.4 | 0.376 |
| 37 | 33 | 31.507 | 0.4 | 0.376 |
| 38 | 33 | 31.506 | 0.4 | 0.377 |
| 39 | 33 | 31.635 | 0.4 | 0.376 |
| 40 | 33 | 31.631 | 0.4 | 0.376 |
| 41 | 33 | 31.611 | 0.4 | 0.377 |
| 42 | 33 | 31.578 | 0.4 | 0.377 |
| 43 | 33 | 31.569 | 0.4 | 0.378 |
| 44 | 33 | 31.564 | 0.4 | 0.377 |
| 45 | 33 | 31.566 | 0.4 | 0.377 |
| 46 | 33 | 31.559 | 0.4 | 0.378 |
| 47 | 33 | 31.552 | 0.4 | 0.377 |
| 48 | 33 | 31.548 | 0.4 | 0.377 |
| 49 | 33 | 31.662 | 0.4 | 0.378 |
| 50 | 33 | 31.658 | 0.4 | 0.378 |
| 51 | 33 | 31.656 | 0.4 | 0.379 |
| 52 | 33 | 32.305 | 0.4 | 0.387 |
| 53 | 33 | 32.304 | 0.4 | 0.387 |
| 54 | 33 | 32.242 | 0.4 | 0.386 |
| 55 | 33 | 32.231 | 0.4 | 0.386 |
| 56 | 33 | 32.231 | 0.4 | 0.386 |
| 57 | 33 | 32.226 | 0.4 | 0.387 |
| 58 | 33 | 32.222 | 0.4 | 0.386 |
| 59 | 33 | 32.219 | 0.4 | 0.386 |
| 60 | 33 | 32.218 | 0.4 | 0.386 |
| 61 | 33 | 32.233 | 0.4 | 0.386 |
| 62 | 33 | 32.201 | 0.4 | 0.386 |
| 63 | 33 | 32.181 | 0.4 | 0.385 |
| 64 | 33 | 32.178 | 0.4 | 0.385 |
| 65 | 33 | 32.176 | 0.4 | 0.385 |
| 66 | 33 | 32.178 | 0.4 | 0.385 |
| 67 | 33 | 32.176 | 0.4 | 0.385 |
| 68 | 33 | 32.174 | 0.4 | 0.385 |
| 69 | 33 | 32.168 | 0.4 | 0.387 |
| 70 | 33 | 32.165 | 0.4 | 0.385 |
| 71 | 33 | 31.611 | 0.4 | 0.377 |
| 72 | 33 | 31.55 | 0.4 | 0.377 |
| 73 | 33 | 31.768 | 0.4 | 0.379 |

Note : the colored values refers to the least low voltages which has more drop of voltages.

2.3.2 Value of maximum loads in table below:(before improvement)

The table below shows the power factor, real and reactive power on each transformer:

| Transformer | Vnom (KV) | Rated (KVA) | Load (KVA) | POWER FACTOR | MOTOR LOAD |  | STATIC LOAD |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | P(KW) | Q(KVAR) | P(KW) | Q(KVAR) |
| 1 | 0.4 | 100 | 65 | 0.79 | 31 | 24 | 21 | 16 |
| 2 | 0.4 | 250 | 175 | 0.90 | 95 | 64 | 63 | 31 |
| 3 | 0.4 | 100 | 75 | 0.88 | 40 | 21 | 26 | 14 |
| 4 | 0.4 | 250 | 200 | 0.93 | 112 | 44 | 74 | 29 |
| 5 | 0.4 | 250 | 170 | 0.92 | 94 | 40 | 63 | 27 |
| 6 | 0.4 | 250 | 200 | 0.99 | 119 | 71 | 79 | 11 |
| 7 | 0.4 | 400 | 300 | 0.92 | 166 | 71 | 110 | 47 |
| 8 | 0.4 | 400 | 305 | 0.95 | 147 | 57 | 116 | 38 |
| 9 | 0.4 | 250 | 150 | 0.93 | 84 | 33 | 56 | 22 |
| 10 | 0.4 | 630 | 400 | 0.93 | 223 | 88 | 149 | 59 |
| 11 | 0.4 | 400 | 310 | 0.70 | 130 | 133 | 87 | 89 |
| 12 | 0.4 | 400 | 280 | 0.89 | 150 | 77 | 100 | 51 |
| 13 | 0.4 | 400 | 270 | 0.90 | 146 | 71 | 97 | 47 |
| 14 | 0.4 | 250 | 190 | 0.88 | 100 | 54 | 67 | 36 |
| 15 | 0.4 | 250 | 150 | 0.86 | 88 | 18 | 59 | 12 |
| 16 | 0.4 | 250 | 120 | 0.98 | 63 | 34 | 42 | 23 |
| 17 | 0.4 | 250 | 160 | 0.88 | 83 | 49 | 55 | 83 |
| 18 | 0.4 | 250 | 170 | 0.86 | 93 | 42 | 62 | 28 |
| 19 | 0.4 | 250 | 180 | 0.91 | 95 | 51 | 63 | 34 |
| 20 | 0.4 | 250 | 120 | 0.88 | 64 | 33 | 43 | 22 |
| 21 | 0.4 | 400 | 330 | 0.89 | 16 | 9 | 11 | 6 |
| 22 | 0.4 | 100 | 30 | 0.88 | 80 | 68 | 53 | 45 |
| 23 | 0.4 | 250 | 175 | 0.76 | 184 | 73 | 123 | 49 |
| 24 | 0.4 | 400 | 255 | 0.93 | 141 | 60 | 94 | 40 |
| 25 | 0.4 | 400 | 350 | 0.92 | 194 | 39 | 129 | 26 |
| 26 | 0.4 | 400 | 300 | 0.98 | 149 | 100 | 100 | 67 |
| 27 | 0.4 | 400 | 220 | 0.83 | 39 | 14 | 26 | 10 |
| 28 | 0.4 | 100 | 70 | 0.94 | 20 | 7 | 13 | 5 |
| 29 | 0.4 | 50 | 35 | 0.94 | 95 | 46 | 63 | 31 |
| 30 | 0.4 | 250 | 175 | 0.90 | 216 | 105 | 144 | 70 |
| 31 | 0.4 | 400 | 400 | 0.90 | 19 | 9 | 13 | 6 |
| 32 | 0.4 | 50 | 35 | 0.91 | 39 | 16 | 26 | 11 |
| 33 | 0.4 | 100 | 70 | 0.92 | 131 | 74 | 87 | 49 |
| 34 | 0.4 | 400 | 250 | 0.87 | 151 | 73 | 101 | 49 |
| 35 | 0.4 | 250 | 175 | 0.90 | 38 | 17 | 25 | 12 |

| Transformer | Vnom (KV) | Rated (KVA) | Load (KVA) | POWER FACTOR | MOTOR LOAD |  | STATIC LOAD |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | P(KW) | Q(KVAR) | P(KW) | Q(KVAR) |
| 36 | 0.4 | 100 | 70 | 0.91 | 162 | 78 | 108 | 52 |
| 37 | 0.4 | 400 | 300 | 0.90 | 32 | 16 | 22 | 10 |
| 38 | 0.4 | 100 | 60 | 0.90 | 31 | 28 | 21 | 19 |
| 39 | 0.4 | 100 | 70 | 0.74 | 35 | 28 | 23 | 19 |
| 40 | 0.4 | 100 | 75 | 0.78 | 158 | 72 | 106 | 48 |
| 41 | 0.4 | 400 | 290 | 0.91 | 166 | 71 | 110 | 47 |
| 42 | 0.4 | 160 | 120 | 0.94 | 68 | 25 | 45 | 16 |
| 43 | 0.4 | 400 | 300 | 0.96 | 173 | 50 | 115 | 34 |
| 44 | 0.4 | 400 | 300 | 0.91 | 153 | 70 | 102 | 46 |
| 45 | 0.4 | 160 | 112 | 0.94 | 63 | 23 | 42 | 15 |
| 46 | 0.4 | 100 | 50 | 0.94 | 28 | 10 | 19 | 7 |
| 47 | 0.4 | 250 | 175 | 0.90 | 95 | 46 | 63 | 31 |
| 48 | 0.4 | 160 | 100 | 0.90 | 95 | 46 | 63 | 31 |
| 49 | 0.4 | 100 | 70 | 0.88 | 54 | 26 | 36 | 17 |
| 50 | 0.4 | 250 | 175 | 0.92 | 37 | 20 | 25 | 13 |
| 51 | 0.4 | 250 | 175 | 0.96 | 97 | 41 | 64 | 27 |
| 52 | 0.4 | 400 | 280 | 0.90 | 101 | 29 | 67 | 20 |
| 53 | 0.4 | 250 | 175 | 0.92 | 151 | 73 | 101 | 49 |
| 54 | 0.4 | 630 | 430 | 0.92 | 97 | 41 | 64 | 27 |
| 55 | 0.4 | 100 | 80 | 0.94 | 237 | 101 | 158 | 67 |
| 56 | 0.4 | 250 | 175 | 0.90 | 45 | 16 | 30 | 11 |
| 57 | 0.4 | 160 | 100 | 0.95 | 95 | 46 | 63 | 31 |
| 58 | 0.4 | 100 | 70 | 0.94 | 57 | 19 | 38 | 12 |
| 59 | 0.4 | 250 | 175 | 0.90 | 39 | 14 | 26 | 10 |
| 60 | 0.4 | 250 | 175 | 0.90 | 95 | 46 | 63 | 31 |
| 61 | 0.4 | 50 | 35 | 0.88 | 95 | 46 | 63 | 31 |
| 62 | 0.4 | 250 | 175 | 0.92 | 18 | 10 | 12 | 7 |
| 63 | 0.4 | 100 | 62 | 0.88 | 97 | 41 | 64 | 27 |
| 64 | 0.4 | 100 | 65 | 0.90 | 33 | 18 | 22 | 12 |
| 65 | 0.4 | 250 | 175 | 0.88 | 35 | 17 | 23 | 11 |
| 66 | 0.4 | 250 | 175 | 0.90 | 92 | 50 | 62 | 33 |
| 67 | 0.4 | 400 | 280 | 0.90 | 95 | 46 | 63 | 31 |
| 68 | 0.4 | 630 | 425 | 0.90 | 151 | 73 | 101 | 49 |
| 69 | 0.4 | 630 | 205 | 0.90 | 230 | 111 | 153 | 74 |
| 70 | 0.4 | 630 | 441 | 0.90 | 111 | 54 | 74 | 36 |
| 71 | 0.4 | 400 | 300 | 0.92 | 238 | 115 | 159 | 57 |
| 72 | 0.4 | 250 | 175 | 0.90 | 90 | 54 | 60 | 36 |
| 73 | 0.4 | 250 | 175 | 0.89 | 93 | 48 | 62 | 32 |

Note : the power factor less than 92% . This causes more penalties on the total bill

2.3.3 SUMMARY

we have to summarize the results, total generation, demand , loading., percentage of losses, and the total power factor.

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 12.308 | 6.106 | 13.740 | 89.6 Lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 12.308 | 6.106 | 13.740 | 89.6 Lag |
| Total Motor Load: | 7.399 | 3.431 | 8.156 | 90.7 lag |
| Total Static Load: | 4.488 | 2.080 |  |  |
| Apparent Losses: | 0.421 | 0.595 |  |  |

The swing current = 240 A

1.the p.f in the   network equal  88.3  and   this value causes   a lot of    problem   specially   paying   banalities   and this value  must be   (0.92-0.95)  the   p.f   is   related to  the current in the network   according that when   the p.f  is  poor  the  current in the network is high this   also can  cause  increasing the  loses in the network .

2. We  will notice in the improvement of the p.f  that when the p.f   increase the current   decrease  then the losses decrease.

3. We   notes  that   the voltage   of   buses  is not   acceptable  and this  voltage will be   less when   it reached the   consumer  and the machine and the substances for the consumer   work   the   rated   approximately  so   this   causes a lot of problem for the consumer.

2.3.4 Problem of the network

1. The P.F is less than 0.92 ; this cause penalties and power losses.

2. There is a voltage drop  and power losses

2.4 The maximum load improvement

we have # of methods in order to improve the network  for  a lot of positive effects  such as  reducing the cost / kwh  . these methods are:

1-  increasing  the  swing  bus  voltage

2-  tab changing in the transformer.

3- adding capacitors to produce reactive power

4- change the connection of the network

.2.4.1  increasing the swing bus voltage

In   the   network   the   connection  point   have   the   flexibility   to increase   the   voltage    on   the   swing   bus   up to 5%   from   the original   voltage   (33 kv)  the   new  value   of   the   swing   bus voltage   equal  (34.65KV)   the   run   of  etab   after   applying   this improvement   the data   shown in the following table:

| Transformer number | Rated Kv | Actual kv | Rated KVA | Load KVA | PF |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.4 | 0.416 | 65 | 67 | 79 |
| 2 | 0.4 | 0.414 | 175 | 180 | 90 |
| 3 | 0.4 | 0.410 | 75 | 77 | 88 |
| 4 | 0.4 | 0.408 | 200 | 203 | 93 |
| 5 | 0.4 | 0.408 | 170 | 173 | 92 |
| 6 | 0.4 | 0.409 | 200 | 204 | 99 |
| 7 | 0.4 | 0.407 | 300 | 304 | 92 |
| 8 | 0.4 | 0.407 | 305 | 309 | 95 |
| 9 | 0.4 | 0.406 | 150 | 152 | 93 |
| 10 | 0.4 | 0.405 | 400 | 404 | 93 |
| 11 | 0.4 | 0.401 | 310 | 310 | 70 |
| 12 | 0.4 | 0.402 | 280 | 281 | 89 |
| 13 | 0.4 | 0.400 | 270 | 270 | 92 |
| 14 | 0.4 | 0.399 | 190 | 190 | 88 |
| 15 | 0.4 | 0.399 | 150 | 175 | 86 |
| 16 | 0.4 | 0.402 | 120 | 150 | 98 |
| 17 | 0.4 | 0.401 | 160 | 120 | 88 |
| 18 | 0.4 | 0.400 | 170 | 160 | 86 |
| 19 | 0.4 | 0.400 | 180 | 170 | 91 |
| 20 | 0.4 | 0.399 | 120 | 180 | 88 |
| 21 | 0.4 | 0.402 | 330 | 120 | 89 |
| 22 | 0.4 | 0.403 | 30 | 30 | 88 |
| 23 | 0.4 | 0.398 | 175 | 174 | 76 |
| 24 | 0.4 | 0.399 | 255 | 329 | 93 |
| 25 | 0.4 | 0.399 | 350 | 255 | 92 |
| 26 | 0.4 | 0.399 | 300 | 329 | 98 |
| 27 | 0.4 | 0.397 | 220 | 298 | 83 |
| 28 | 0.4 | 0.398 | 70 | 70 | 94 |
| 29 | 0.4 | 0.397 | 35 | 35 | 94 |
| 30 | 0.4 | 0.396 | 175 | 174 | 90 |
| 31 | 0.4 | 0.395 | 400 | 396 | 90 |
| 32 | 0.4 | 0.397 | 35 | 35 | 91 |
| 33 | 0.4 | 0.397 | 70 | 70 | 92 |
| 34 | 0.4 | 0.397 | 250 | 248 | 87 |
| 35 | 0.4 | 0.394 | 175 | 277 | 90 |
| 36 | 0.4 | 0.397 | 70 | 70 | 91 |
| 37 | 0.4 | 0.396 | 300 | 298 | 90 |
| 38 | 0.4 | 0.397 | 60 | 60 | 90 |
| 39 | 0.4 | 0.397 | 70 | 70 | 74 |
| 40 | 0.4 | 0.397 | 75 | 74 | 78 |
| 41 | 0.4 | 0.398 | 290 | 289 | 91 |
| 42 | 0.4 | 0.398 | 120 | 119 | 94 |
| 43 | 0.4 | 0.398 | 300 | 299 | 96 |
| 44 | 0.4 | 0.397 | 300 | 278 | 91 |
| 45 | 0.4 | 0.398 | 112 | 111 | 94 |
| 46 | 0.4 | 0.398 | 50 | 50 | 94 |
| 47 | 0.4 | 0.397 | 175 | 174 | 90 |
| 48 | 0.4 | 0.397 | 100 | 99 | 90 |
| 49 | 0.4 | 0.398 | 70 | 70 | 88 |
| 50 | 0.4 | 0.399 | 175 | 175 | 92 |
| 51 | 0.4 | 0.399 | 175 | 175 | 96 |
| 52 | 0.4 | 0.407 | 280 | 284 | 90 |
| 53 | 0.4 | 0.407 | 175 | 178 | 92 |
| 54 | 0.4 | 0.406 | 430 | 436 | 92 |
| 55 | 0.4 | 0.406 | 80 | 81 | 94 |
| 56 | 0.4 | 0.406 | 175 | 177 | 90 |
| 57 | 0.4 | 0.407 | 100 | 101 | 95 |
| 58 | 0.4 | 0.406 | 70 | 71 | 94 |
| 59 | 0.4 | 0.406 | 175 | 177 | 90 |
| 60 | 0.4 | 0.406 | 175 | 177 | 90 |
| 61 | 0.4 | 0.406 | 35 | 35 | 88 |
| 62 | 0.4 | 0.406 | 175 | 177 | 92 |
| 63 | 0.4 | 0.406 | 62 | 63 | 88 |
| 64 | 0.4 | 0.406 | 65 | 66 | 90 |
| 65 | 0.4 | 0.405 | 175 | 177 | 88 |
| 66 | 0.4 | 0.405 | 175 | 177 | 90 |
| 67 | 0.4 | 0.405 | 280 | 283 | 90 |
| 68 | 0.4 | 0.405 | 425 | 430 | 90 |
| 69 | 0.4 | 0.407 | 205 | 208 | 90 |
| 70 | 0.4 | 0.405 | 441 | 446 | 90 |
| 71 | 0.4 | 0.398 | 300 | 299 | 92 |
| 72 | 0.4 | 0.397 | 175 | 174 | 90 |
| 73 | 0.4 | 0.400 | 175 | 175 | 89 |

This   table   shows   the   bus voltage  after   increasing  the  swing  bus voltage.

But we can't apply this method because the control of swing bus only by IEC

2.4.2 improvement the max. case using tap changing

In this   method   of  tab   changing    involves   changing    in  the   tab ratio  on t he transformer    but in   limiting   rang   which not   accede (5% ).

And   after   we   applying   this   method   we   have the following   result   as  shown  I  the  table   below :

| Transformer number | Rated kv | Actual kv | Rated KVA | Actual KVA | PF |
| --- | --- | --- | --- | --- | --- |
| 1 | 0.4 | 0.415 | 65 | 67 | 79 |
| 2 | 0.4 | 0.414 | 175 | 188 | 90 |
| 3 | 0.4 | 0.413 | 75 | 79 | 88 |
| 4 | 0.4 | 0.415 | 200 | 206 | 93 |
| 5 | 0.4 | 0.415 | 170 | 175 | 92 |
| 6 | 0.4 | 0.416 | 200 | 206 | 99 |
| 7 | 0.4 | 0.413 | 300 | 308 | 92 |
| 8 | 0.4 | 0.413 | 305 | 313 | 95 |
| 9 | 0.4 | 0.413 | 150 | 154 | 93 |
| 10 | 0.4 | 0.416 | 400 | 413 | 93 |
| 11 | 0.4 | 0.419 | 310 | 322 | 70 |
| 12 | 0.4 | 0.416 | 280 | 289 | 89 |
| 13 | 0.4 | 0.419 | 270 | 280 | 92 |
| 14 | 0.4 | 0.418 | 190 | 197 | 88 |
| 15 | 0.4 | 0.418 | 150 | 181 | 86 |
| 16 | 0.4 | 0.416 | 120 | 155 | 98 |
| 17 | 0.4 | 0.419 | 160 | 125 | 88 |
| 18 | 0.4 | 0.418 | 170 | 166 | 86 |
| 19 | 0.4 | 0.418 | 180 | 176 | 91 |
| 20 | 0.4 | 0.418 | 120 | 186 | 88 |
| 21 | 0.4 | 0.416 | 330 | 124 | 89 |
| 22 | 0.4 | 0.417 | 30 | 31 | 88 |
| 23 | 0.4 | 0.416 | 175 | 181 | 76 |
| 24 | 0.4 | 0.417 | 255 | 341 | 93 |
| 25 | 0.4 | 0.417 | 350 | 264 | 92 |
| 26 | 0.4 | 0.417 | 300 | 341 | 98 |
| 27 | 0.4 | 0.415 | 220 | 309 | 83 |
| 28 | 0.4 | 0.416 | 70 | 72 | 94 |
| 29 | 0.4 | 0.415 | 35 | 36 | 94 |
| 30 | 0.4 | 0.414 | 175 | 180 | 90 |
| 31 | 0.4 | 0.412 | 400 | 410 | 90 |
| 32 | 0.4 | 0.414 | 35 | 36 | 91 |
| 33 | 0.4 | 0.414 | 70 | 72 | 92 |
| 34 | 0.4 | 0.414 | 250 | 257 | 87 |
| 35 | 0.4 | 0.411 | 175 | 287 | 90 |
| 36 | 0.4 | 0.414 | 70 | 72 | 91 |
| 37 | 0.4 | 0.414 | 300 | 308 | 90 |
| 38 | 0.4 | 0.414 | 60 | 62 | 90 |
| 39 | 0.4 | 0.415 | 70 | 72 | 74 |
| 40 | 0.4 | 0.414 | 75 | 77 | 78 |
| 41 | 0.4 | 0.416 | 290 | 299 | 91 |
| 42 | 0.4 | 0.415 | 120 | 124 | 94 |
| 43 | 0.4 | 0.416 | 300 | 310 | 96 |
| 44 | 0.4 | 0.415 | 300 | 289 | 91 |
| 45 | 0.4 | 0.415 | 112 | 116 | 94 |
| 46 | 0.4 | 0.416 | 50 | 52 | 94 |
| 47 | 0.4 | 0.415 | 175 | 180 | 90 |
| 48 | 0.4 | 0.415 | 100 | 103 | 90 |
| 49 | 0.4 | 0.416 | 70 | 72 | 88 |
| 50 | 0.4 | 0.417 | 175 | 181 | 92 |
| 51 | 0.4 | 0.417 | 175 | 180 | 96 |
| 52 | 0.4 | 0.418 | 280 | 290 | 90 |
| 53 | 0.4 | 0.418 | 175 | 181 | 92 |
| 54 | 0.4 | 0.417 | 430 | 445 | 92 |
| 55 | 0.4 | 0.417 | 80 | 83 | 94 |
| 56 | 0.4 | 0.417 | 175 | 181 | 90 |
| 57 | 0.4 | 0.418 | 100 | 104 | 95 |
| 58 | 0.4 | 0.417 | 70 | 72 | 94 |
| 59 | 0.4 | 0.417 | 175 | 181 | 90 |
| 60 | 0.4 | 0.417 | 175 | 181 | 90 |
| 61 | 0.4 | 0.417 | 35 | 36 | 88 |
| 62 | 0.4 | 0.417 | 175 | 181 | 92 |
| 63 | 0.4 | 0.416 | 62 | 64 | 88 |
| 64 | 0.4 | 0.416 | 65 | 67 | 90 |
| 65 | 0.4 | 0.416 | 175 | 181 | 88 |
| 66 | 0.4 | 0.416 | 175 | 181 | 90 |
| 67 | 0.4 | 0.416 | 280 | 289 | 90 |
| 68 | 0.4 | 0.416 | 425 | 439 | 90 |
| 69 | 0.4 | 0.418 | 205 | 213 | 90 |
| 70 | 0.4 | 0.416 | 441 | 455 | 90 |
| 71 | 0.4 | 0.416 | 300 | 310 | 92 |
| 72 | 0.4 | 0.415 | 175 | 180 | 90 |
| 73 | 0.4 | 0.418 | 175 | 181 | 89 |

This table show that the volteges of buses after improvement by changing the taps of transformer.

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 13.215 | 6.574 | 14.760 | 89.5 lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 13.215 | 6.574 | 14.760 | 89.5 lag |
| Total Motor Load: | 7.399 | 3.431 | 8.156 | 90.7 lag |
| Total Static Load: | 5.332 | 2.473 |  |  |
| Apparent Losses: | 0.485 | 0.669 |  |  |

The swing current = 258 A

Representing the total demand….. losses ,and whole PF  for the tap changing improvement.

2.4.3 Power factor improvement

The cosine of angle of Phase displacement between voltage and current in an AC circuit is known as Power Factor. The Reactive component is a measure of the Power Factor.  Under normal operating conditions certain electrical loads (e.g. induction motors, welding equipment, arc furnaces and fluorescent lighting (draw not only active power from the supply (kilowatts, kW) but also reactive power (reactive KVAR). This reactive power is necessary for the equipment to operate correctly but could be interpreted as an undesirable burden on the supply.

How to improve the P.F?

Where:

- Qc: the reactive power to be compensated by the capacitor.

- P: the real power of the load.

- Ø old: the actual power angle.

- Ø New: the proposed power angle.

Capacitor banks

The important method of improvement power factor is by adding shunt capacitor banks at the buses at both transmission and distribution levels and loads and there are more effective to add them in the low level voltages.

Effect of Low Power Factor

1.Higher Apparent Current

2.Higher Losses in the Electrical Distribution network

3.Low Voltage in the network

Benefits of Improving Power Factor

1.Lower Apparent Power.

2. Reduces losses in the transmission line  .

3. Improves voltage drop.

4.Reduces load factor on transformers.

5.Avoiding the penalties.

The problem of low power factor

The  low P.F is highly undesirable as it causes an increase in current, resulting in additional losses of active power in all the elements of power system from power station generator down to the utilization devices.In addition to the losses the low P.F causes penalties, for example for every 1% P.F below 92% and above 80% costs us 1% of the total bill.

The power factor improvement for max. load

-- our aim to improvement of p .f in order to avoid penalties and ton reduce the current flow in the network which reduce the electrical losses in the network

-- the power factor after the improving must be in the range (0.92- 0.95)

--  we use this equation to calculate  the  reactive  power needing for this improvement is:

Qc  = P(tan cos (p.f old)- tan cos (p.f new))

PF old = 89.5

PF new at least = 92%

Q=13.215 (tan (26.49) – tan(23.074)) = 957 KVAR

The capacitor is added in delta connection parallel to the transformer in secendary side(0.4 kv).

The table below shows the voltage level before and after adding the capacitance:

| Transformer number | voltage(rated) kv | Q(KVAR) | voltage(actual) before add. capacitors | voltage(rated) after add. capacitors | Pf before | Pf after |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.4 | 30 | 0.415 | 0.418 | 79 | 98 |
| 2 | 0.4 | 50 | 0.414 | 0.416 | 90 | 98 |
| 3 | 0.4 | 20 | 0.413 | 0.416 | 88 | 97 |
| 4 | 0.4 |  | 0.415 | 0.415 | 93 | 93 |
| 5 | 0.4 |  | 0.415 | 0.415 | 92 | 92 |
| 6 | 0.4 |  | 0.416 | 0.416 | 99 | 99 |
| 7 | 0.4 |  | 0.413 | 0.413 | 92 | 92 |
| 8 | 0.4 |  | 0.413 | 0.413 | 95 | 95 |
| 9 | 0.4 |  | 0.413 | 0.413 | 93 | 93 |
| 10 | 0.4 |  | 0.416 | 0.416 | 93 | 93 |
| 11 | 0.4 | 150 | 0.419 | 0.424 | 70 | 96 |
| 12 | 0.4 | 50 | 0.416 | 0.418 | 89 | 95 |
| 13 | 0.4 |  | 0.419 | 0.419 | 92 | 92 |
| 14 | 0.4 | 25 | 0.418 | 0.420 | 88 | 93 |
| 15 | 0.4 | 30 | 0.418 | 0.420 | 86 | 93 |
| 16 | 0.4 |  | 0.416 | 0.416 | 98 | 98 |
| 17 | 0.4 | 15 | 0.419 | 0.421 | 88 | 93 |
| 18 | 0.4 | 30 | 0.418 | 0.420 | 86 | 93 |
| 19 | 0.4 |  | 0.418 | 0.418 | 91 | 91 |
| 20 | 0.4 | 20 | 0.418 | 0.419 | 88 | 92 |
| 21 | 0.4 | 15 | 0.416 | 0.417 | 89 | 94 |
| 22 | 0.4 |  | 0.417 | 0.417 | 88 | 88 |
| 23 | 0.4 | 60 | 0.416 | 0.419 | 76 | 93 |
| 24 | 0.4 |  | 0.417 | 0.417 | 93 | 93 |
| 25 | 0.4 |  | 0.417 | 0.417 | 92 | 92 |
| 26 | 0.4 |  | 0.417 | 0.417 | 98 | 98 |
| 27 | 0.4 | 65 | 0.415 | 0.417 | 83 | 92 |
| 28 | 0.4 |  | 0.416 | 0.416 | 94 | 94 |
| 29 | 0.4 |  | 0.415 | 0.415 | 94 | 94 |
| 30 | 0.4 |  | 0.414 | 0.414 | 90 | 90 |
| 31 | 0.4 |  | 0.412 | 0.412 | 90 | 90 |
| 32 | 0.4 |  | 0.414 | 0.414 | 91 | 91 |
| 33 | 0.4 |  | 0.414 | 0.414 | 92 | 92 |
| 34 | 0.4 | 50 | 0.414 | 0.417 | 87 | 94 |
| 35 | 0.4 | 30 | 0.411 | 0.414 | 90 | 93 |
| 36 | 0.4 |  | 0.414 | 0.414 | 91 | 91 |
| 37 | 0.4 | 30 | 0.414 | 0.415 | 90 | 93 |
| 38 | 0.4 |  | 0.414 | 0.414 | 90 | 90 |
| 39 | 0.4 | 30 | 0.415 | 0.418 | 74 | 95 |
| 40 | 0.4 | 25 | 0.414 | 0.418 | 78 | 94 |
| 41 | 0.4 |  | 0.416 | 0.416 | 91 | 91 |
| 42 | 0.4 |  | 0.415 | 0.415 | 94 | 94 |
| 43 | 0.4 |  | 0.416 | 0.416 | 96 | 96 |
| 44 | 0.4 |  | 0.415 | 0.415 | 91 | 91 |
| 45 | 0.4 |  | 0.415 | 0.415 | 94 | 94 |
| 46 | 0.4 |  | 0.416 | 0.416 | 94 | 94 |
| 47 | 0.4 |  | 0.415 | 0.415 | 90 | 90 |
| 48 | 0.4 |  | 0.415 | 0.415 | 90 | 90 |
| 49 | 0.4 | 15 | 0.416 | 0.419 | 88 | 96 |
| 50 | 0.4 |  | 0.417 | 0.417 | 92 | 92 |
| 51 | 0.4 |  | 0.417 | 0.417 | 96 | 96 |
| 52 | 0.4 |  | 0.418 | 0.418 | 90 | 90 |
| 53 | 0.4 |  | 0.418 | 0.418 | 92 | 92 |
| 54 | 0.4 |  | 0.417 | 0.417 | 92 | 92 |
| 55 | 0.4 |  | 0.417 | 0.417 | 94 | 94 |
| 56 | 0.4 |  | 0.417 | 0.417 | 90 | 90 |
| 57 | 0.4 |  | 0.418 | 0.418 | 95 | 95 |
| 58 | 0.4 |  | 0.417 | 0.417 | 94 | 94 |
| 59 | 0.4 |  | 0.417 | 0.417 | 90 | 90 |
| 60 | 0.4 |  | 0.417 | 0.417 | 90 | 90 |
| 61 | 0.4 |  | 0.417 | 0.417 | 88 | 88 |
| 62 | 0.4 |  | 0.417 | 0.417 | 92 | 92 |
| 63 | 0.4 |  | 0.416 | 0.416 | 88 | 88 |
| 64 | 0.4 |  | 0.416 | 0.416 | 90 | 90 |
| 65 | 0.4 | 30 | 0.416 | 0.417 | 88 | 94 |
| 66 | 0.4 | 30 | 0.416 | 0.418 | 90 | 96 |
| 67 | 0.4 | 30 | 0.416 | 0.417 | 90 | 93 |
| 68 | 0.4 |  | 0.416 | 0.416 | 90 | 90 |
| 69 | 0.4 | 20 | 0.418 | 0.419 | 90 | 93 |
| 70 | 0.4 |  | 0.416 | 0.416 | 90 | 90 |
| 71 | 0.4 |  | 0.416 | 0.416 | 92 | 92 |
| 72 | 0.4 |  | 0.415 | 0.415 | 90 | 90 |
| 73 | 0.4 |  | 0.418 | 0.418 | 89 | 89 |

The result of basic information of the network after adding capacitance:

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 13.222 | 5.623 | 14.368 | 92.0lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 13.222 | 5.623 | 14.368 | 92.0lag |
| Total Motor Load: | 7.399 | 3.431 | 8.156 | 90.7 lag |
| Total Static Load: | 5.363 | 1.558 |  |  |
| Apparent Losses: | 0.460 | 0.634 |  |  |

The swing current = 251A

We note:

when we increase power factor the losses in the network decrease and the total current decrease .

Losses before p.f improvement = 0.485 Mw .

Losses after p.f improvement = 0.460Mw .

Total current in origin case = 258A

Total current before voltage improvement= 251 A

2.4.4 the voltage level improvement using capacitors

| Transformer number | voltage(rated) kv | Q(KVAR) | voltage(actual) before add. capacitors | voltage(rated) after add. capacitors | Pf before | Pf after |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.4 | 30 | 0.396 | 0.398 | 79 | 98 |
| 2 | 0.4 | 30 | 0.394 | 0.395 | 90 | 95 |
| 3 | 0.4 | 20 | 0.390 | 0.392 | 88 | 97 |
| 4 | 0.4 |  | 0.388 | 0.388 | 93 | 93 |
| 5 | 0.4 |  | 0.388 | 0.388 | 92 | 92 |
| 6 | 0.4 |  | 0.389 | 0.389 | 99 | 99 |
| 7 | 0.4 |  | 0.387 | 0.387 | 92 | 92 |
| 8 | 0.4 |  | 0.387 | 0.387 | 95 | 95 |
| 9 | 0.4 |  | 0.386 | 0.386 | 93 | 93 |
| 10 | 0.4 |  | 0.385 | 0.385 | 93 | 93 |
| 11 | 0.4 | 150 | 0.380 | 0.384 | 70 | 94 |
| 12 | 0.4 | 80 | 0.382 | 0.384 | 89 | 98 |
| 13 | 0.4 | 20 | 0.380 | 0.381 | 90 | 92.5 |
| 14 | 0.4 | 50 | 0.379 | 0.381 | 88 | 96 |
| 15 | 0.4 | 50 | 0.379 | 0.381 | 86 | 96 |
| 16 | 0.4 |  | 0.381 | 0.381 | 98 | 98 |
| 17 | 0.4 | 30 | 0.381 | 0.382 | 88 | 96 |
| 18 | 0.4 | 50 | 0.379 | 0.382 | 86 | 97 |
| 19 | 0.4 |  | 0.380 | 0.380 | 91 | 91 |
| 20 | 0.4 | 30 | 0.379 | 0.381 | 88 | 94 |
| 21 | 0.4 | 30 | 0.382 | 0.383 | 89 | 97 |
| 22 | 0.4 | 10 | 0.382 | 0.384 | 88 | 98 |
| 23 | 0.4 | 80 | 0.378 | 0.381 | 76 | 96 |
| 24 | 0.4 |  | 0.378 | 0.378 | 93 | 93 |
| 25 | 0.4 |  | 0.379 | 0.379 | 92 | 92 |
| 26 | 0.4 |  | 0.379 | 0.379 | 98 | 98 |
| 27 | 0.4 | 100 | 0.376 | 0.379 | 83 | 96 |
| 28 | 0.4 |  | 0.377 | 0.378 | 94 | 94 |
| 29 | 0.4 |  | 0.377 | 0.378 | 94 | 94 |
| 30 | 0.4 | 30 | 0.376 | 0.378 | 90 | 95 |
| 31 | 0.4 | 80 | 0.374 | 0.377 | 90 | 95 |
| 32 | 0.4 | 10 | 0.376 | 0.379 | 91 | 98 |
| 33 | 0.4 | 15 | 0.377 | 0.379 | 92 | 98 |
| 34 | 0.4 | 80 | 0.376 | 0.379 | 87 | 97 |
| 35 | 0.4 | 80 | 0.374 | 0.378 | 90 | 97 |
| 36 | 0.4 | 20 | 0.376 | 0.380 | 91 | 98 |
| 37 | 0.4 | 80 | 0.376 | 0.379 | 90 | 98 |
| 38 | 0.4 | 20 | 0.377 | 0.380 | 90 | 99 |
| 39 | 0.4 | 30 | 0.376 | 0.380 | 74 | 94 |
| 40 | 0.4 | 30 | 0.376 | 0.380 | 78 | 95 |
| 41 | 0.4 | 30 | 0.377 | 0.380 | 91 | 94 |
| 42 | 0.4 |  | 0.377 | 0.377 | 94 | 94 |
| 43 | 0.4 |  | 0.378 | 0.378 | 96 | 96 |
| 44 | 0.4 | 50 | 0.377 | 0.380 | 91 | 96 |
| 45 | 0.4 |  | 0.377 | 0.377 | 94 | 94 |
| 46 | 0.4 |  | 0.378 | 0.378 | 94 | 94 |
| 47 | 0.4 | 30 | 0.377 | 0.379 | 90 | 95 |
| 48 | 0.4 | 30 | 0.377 | 0.380 | 90 | 98 |
| 49 | 0.4 | 20 | 0.378 | 0.381 | 88 | 97 |
| 50 | 0.4 |  | 0.378 | 0.378 | 92 | 92 |
| 51 | 0.4 |  | 0.379 | 0.379 | 96 | 96 |
| 52 | 0.4 | 50 | 0.387 | 0.389 | 90 | 96 |
| 53 | 0.4 |  | 0.387 | 0.387 | 92 | 92 |
| 54 | 0.4 |  | 0.386 | 0.386 | 92 | 92 |
| 55 | 0.4 |  | 0.386 | 0.386 | 94 | 94 |
| 56 | 0.4 | 50 | 0.386 | 0.388 | 90 | 98 |
| 57 | 0.4 |  | 0.387 | 0.387 | 95 | 95 |
| 58 | 0.4 |  | 0.386 | 0.386 | 94 | 94 |
| 59 | 0.4 | 30 | 0.386 | 0.388 | 90 | 95 |
| 60 | 0.4 | 30 | 0.386 | 0.387 | 90 | 95 |
| 61 | 0.4 | 10 | 0.386 | 0.388 | 88 | 97 |
| 62 | 0.4 |  | 0.386 | 0.386 | 92 | 92 |
| 63 | 0.4 | 20 | 0.385 | 0.387 | 88 | 98 |
| 64 | 0.4 | 20 | 0.385 | 0.388 | 90 | 98 |
| 65 | 0.4 | 30 | 0.385 | 0.386 | 88 | 93 |
| 66 | 0.4 | 50 | 0.385 | 0.388 | 90 | 98 |
| 67 | 0.4 | 80 | 0.385 | 0.388 | 90 | 98 |
| 68 | 0.4 | 100 | 0.385 | 0.388 | 90 | 97 |
| 69 | 0.4 | 50 | 0.387 | 0.389 | 90 | 97 |
| 70 | 0.4 | 80 | 0.385 | 0.387 | 90 | 96 |
| 71 | 0.4 | 30 | 0.377 | 0.380 | 92 | 95 |
| 72 | 0.4 | 30 | 0.377 | 0.379 | 90 | 95 |
| 73 | 0.4 | 50 | 0.379 | 0.382 | 89 | 97 |

The result of basic information of the network after adding capacitance:

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 12.322 | 4.132 | 12.996 | 94.8lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 12.322 | 4.132 | 12.996 | 94.8lag |
| Total Motor Load: | 7.399 | 3.431 | 8.156 | 90.7 lag |
| Total Static Load: | 4.548 | 0.169 |  |  |
| Apparent Losses: | 0.375 | 0.531 |  |  |

2.4.5 Comparison between three case

1.   the origin case .

2.   power factor improvement  case .

3.   improvement  using tap.

| Transformer number | Voltage Orginal case | Voltage Improve By tap | Pf improvement case. |
| --- | --- | --- | --- |
| 1 | 0.396 | 0.415 | 0.418 |
| 2 | 0.394 | 0.414 | 0.416 |
| 3 | 0.390 | 0.413 | 0.416 |
| 4 | 0.388 | 0.415 | 0.415 |
| 5 | 0.388 | 0.415 | 0.415 |
| 6 | 0.389 | 0.416 | 0.416 |
| 7 | 0.387 | 0.413 | 0.413 |
| 8 | 0.387 | 0.413 | 0.413 |
| 9 | 0.386 | 0.413 | 0.413 |
| 10 | 0.385 | 0.416 | 0.416 |
| 11 | 0.380 | 0.419 | 0.424 |
| 12 | 0.382 | 0.416 | 0.418 |
| 13 | 0.380 | 0.419 | 0.419 |
| 14 | 0.379 | 0.418 | 0.420 |
| 15 | 0.379 | 0.418 | 0.420 |
| 16 | 0.381 | 0.416 | 0.416 |
| 17 | 0.381 | 0.419 | 0.421 |
| 18 | 0.379 | 0.418 | 0.420 |
| 19 | 0.380 | 0.418 | 0.418 |
| 20 | 0.379 | 0.418 | 0.419 |
| 21 | 0.382 | 0.416 | 0.417 |
| 22 | 0.382 | 0.417 | 0.417 |
| 23 | 0.378 | 0.416 | 0.419 |
| 24 | 0.378 | 0.417 | 0.417 |
| 25 | 0.379 | 0.417 | 0.417 |
| 26 | 0.379 | 0.417 | 0.417 |
| 27 | 0.376 | 0.415 | 0.417 |
| 28 | 0.377 | 0.416 | 0.416 |
| 29 | 0.377 | 0.415 | 0.415 |
| 30 | 0.376 | 0.414 | 0.414 |
| 31 | 0.374 | 0.412 | 0.412 |
| 32 | 0.376 | 0.414 | 0.414 |
| 33 | 0.377 | 0.414 | 0.414 |
| 34 | 0.376 | 0.414 | 0.417 |
| 35 | 0.374 | 0.411 | 0.414 |
| 36 | 0.376 | 0.414 | 0.414 |
| 37 | 0.376 | 0.414 | 0.415 |
| 38 | 0.377 | 0.414 | 0.414 |
| 39 | 0.376 | 0.415 | 0.418 |
| 40 | 0.376 | 0.414 | 0.418 |
| 41 | 0.377 | 0.416 | 0.416 |
| 42 | 0.377 | 0.415 | 0.415 |
| 43 | 0.378 | 0.416 | 0.416 |
| 44 | 0.377 | 0.415 | 0.415 |
| 45 | 0.377 | 0.415 | 0.415 |
| 46 | 0.378 | 0.416 | 0.416 |
| 47 | 0.377 | 0.415 | 0.415 |
| 48 | 0.377 | 0.415 | 0.415 |
| 49 | 0.378 | 0.416 | 0.419 |
| 50 | 0.378 | 0.417 | 0.417 |
| 51 | 0.379 | 0.417 | 0.417 |
| 52 | 0.387 | 0.418 | 0.418 |
| 53 | 0.387 | 0.418 | 0.418 |
| 54 | 0.386 | 0.417 | 0.417 |
| 55 | 0.386 | 0.417 | 0.417 |
| 56 | 0.386 | 0.417 | 0.417 |
| 57 | 0.387 | 0.418 | 0.418 |
| 58 | 0.386 | 0.417 | 0.417 |
| 59 | 0.386 | 0.417 | 0.417 |
| 60 | 0.386 | 0.417 | 0.417 |
| 61 | 0.386 | 0.417 | 0.417 |
| 62 | 0.386 | 0.417 | 0.417 |
| 63 | 0.385 | 0.416 | 0.416 |
| 64 | 0.385 | 0.416 | 0.416 |
| 65 | 0.385 | 0.416 | 0.417 |
| 66 | 0.385 | 0.416 | 0.418 |
| 67 | 0.385 | 0.416 | 0.417 |
| 68 | 0.385 | 0.416 | 0.416 |
| 69 | 0.387 | 0.418 | 0.419 |
| 70 | 0.385 | 0.416 | 0.416 |
| 71 | 0.377 | 0.416 | 0.416 |
| 72 | 0.377 | 0.415 | 0.415 |
| 73 | 0.379 | 0.418 | 0.418 |

Chapter three:

3.1 Minimum case:

Value of minimum loads in table below:(before improvement)

| Transformer | Vnom (KV) | Rated (KVA) | Load (KVA) | POWER FACTOR | MOTOR LOAD |  | STATIC LOAD |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | P(KW) | Q(KVAR) | P(KW) | Q(KVAR) |
| 1 | 0.4 | 100 | 26 | 0.79 | 12 | 10 | 8 | 6 |
| 2 | 0.4 | 250 | 70 | 0.90 | 38 | 18 | 25 | 12 |
| 3 | 0.4 | 100 | 30 | 0.88 | 16 | 9 | 11 | 6 |
| 4 | 0.4 | 250 | 79 | 0.93 | 45 | 18 | 30 | 12 |
| 5 | 0.4 | 250 | 67 | 0.92 | 38 | 16 | 25 | 11 |
| 6 | 0.4 | 250 | 79 | 0.99 | 48 | 7 | 32 | 5 |
| 7 | 0.4 | 400 | 119 | 0.92 | 26 | 28 | 44 | 19 |
| 8 | 0.4 | 400 | 121 | 0.95 | 70 | 23 | 46 | 15 |
| 9 | 0.4 | 250 | 59 | 0.93 | 33 | 13 | 22 | 9 |
| 10 | 0.4 | 630 | 158 | 0.93 | 89 | 35 | 60 | 24 |
| 11 | 0.4 | 400 | 122 | 0.70 | 52 | 53 | 35 | 35 |
| 12 | 0.4 | 400 | 110 | 0.89 | 60 | 31 | 40 | 20 |
| 13 | 0.4 | 400 | 106 | 0.90 | 58 | 28 | 39 | 19 |
| 14 | 0.4 | 250 | 75 | 0.88 | 40 | 22 | 27 | 14 |
| 15 | 0.4 | 250 | 69 | 0.86 | 35 | 7 | 24 | 5 |
| 16 | 0.4 | 250 | 59 | 0.98 | 25 | 14 | 17 | 9 |
| 17 | 0.4 | 250 | 47 | 0.88 | 33 | 20 | 22 | 13 |
| 18 | 0.4 | 250 | 63 | 0.86 | 37 | 17 | 25 | 11 |
| 19 | 0.4 | 250 | 67 | 0.91 | 38 | 21 | 25 | 14 |
| 20 | 0.4 | 250 | 71 | 0.88 | 26 | 13 | 17 | 9 |
| 21 | 0.4 | 400 | 47 | 0.89 | 6 | 3 | 4 | 2 |
| 22 | 0.4 | 100 | 12 | 0.88 | 32 | 27 | 21 | 18 |
| 23 | 0.4 | 250 | 69 | 0.76 | 74 | 29 | 49 | 19 |
| 24 | 0.4 | 400 | 130 | 0.93 | 56 | 24 | 38 | 16 |
| 25 | 0.4 | 400 | 100 | 0.92 | 78 | 16 | 52 | 11 |
| 26 | 0.4 | 400 | 130 | 0.98 | 60 | 40 | 40 | 27 |
| 27 | 0.4 | 400 | 118 | 0.83 | 16 | 6 | 11 | 4 |
| 28 | 0.4 | 100 | 28 | 0.94 | 8 | 3 | 5 | 2 |
| 29 | 0.4 | 50 | 14 | 0.94 | 38 | 18 | 25 | 12 |
| 30 | 0.4 | 250 | 69 | 0.90 | 86 | 42 | 58 | 28 |
| 31 | 0.4 | 400 | 157 | 0.90 | 8 | 3 | 5 | 2 |
| 32 | 0.4 | 50 | 14 | 0.91 | 15 | 7 | 10 | 4 |
| 33 | 0.4 | 100 | 27 | 0.92 | 52 | 30 | 35 | 02 |
| 34 | 0.4 | 400 | 98 | 0.87 | 60 | 29 | 40 | 20 |
| 35 | 0.4 | 250 | 110 | 0.90 | 15 | 7 | 10 | 5 |

| Transformer | Vnom (KV) | Rated (KVA) | Load (KVA) | POWER FACTOR | MOTOR LOAD |  | STATIC LOAD |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | P(KW) | Q(KVAR) | P(KW) | Q(KVAR) |
| 36 | 0.4 | 100 | 27 | 0.91 | 65 | 31 | 43 | 21 |
| 37 | 0.4 | 400 | 118 | 0.90 | 13 | 6 | 9 | 4 |
| 38 | 0.4 | 100 | 24 | 0.90 | 12 | 11 | 8 | 8 |
| 39 | 0.4 | 100 | 27 | 0.74 | 14 | 11 | 9 | 8 |
| 40 | 0.4 | 100 | 29 | 0.78 | 63 | 29 | 42 | 19 |
| 41 | 0.4 | 400 | 114 | 0.91 | 66 | 28 | 44 | 19 |
| 42 | 0.4 | 160 | 47 | 0.94 | 27 | 10 | 18 | 7 |
| 43 | 0.4 | 400 | 118 | 0.96 | 69 | 20 | 46 | 13 |
| 44 | 0.4 | 400 | 110 | 0.91 | 61 | 28 | 41 | 19 |
| 45 | 0.4 | 160 | 44 | 0.94 | 25 | 9 | 17 | 6 |
| 46 | 0.4 | 100 | 20 | 0.94 | 11 | 4 | 8 | 3 |
| 47 | 0.4 | 250 | 68 | 0.90 | 32 | 15 | 32 | 15 |
| 48 | 0.4 | 160 | 39 | 0.90 | 38 | 18 | 25 | 12 |
| 49 | 0.4 | 100 | 28 | 0.88 | 22 | 10 | 14 | 7 |
| 50 | 0.4 | 250 | 69 | 0.92 | 15 | 8 | 10 | 5 |
| 51 | 0.4 | 250 | 69 | 0.96 | 39 | 61 | 26 | 11 |
| 52 | 0.4 | 400 | 111 | 0.90 | 40 | 12 | 27 | 8 |
| 53 | 0.4 | 250 | 69 | 0.92 | 60 | 29 | 40 | 20 |
| 54 | 0.4 | 630 | 170 | 0.92 | 39 | 16 | 26 | 11 |
| 55 | 0.4 | 100 | 32 | 0.94 | 95 | 40 | 63 | 27 |
| 56 | 0.4 | 250 | 69 | 0.90 | 18 | 7 | 12 | 4 |
| 57 | 0.4 | 160 | 40 | 0.95 | 38 | 18 | 25 | 12 |
| 58 | 0.4 | 100 | 28 | 0.94 | 23 | 7 | 15 | 5 |
| 59 | 0.4 | 250 | 69 | 0.90 | 16 | 6 | 11 | 4 |
| 60 | 0.4 | 250 | 69 | 0.90 | 25 | 12 | 38 | 18 |
| 61 | 0.4 | 50 | 14 | 0.88 | 38 | 18 | 25 | 21 |
| 62 | 0.4 | 250 | 69 | 0.92 | 7 | 4 | 5 | 3 |
| 63 | 0.4 | 100 | 25 | 0.88 | 39 | 16 | 26 | 11 |
| 64 | 0.4 | 100 | 26 | 0.90 | 13 | 7 | 9 | 5 |
| 65 | 0.4 | 250 | 69 | 0.88 | 14 | 7 | 9 | 5 |
| 66 | 0.4 | 250 | 69 | 0.90 | 37 | 20 | 25 | 13 |
| 67 | 0.4 | 400 | 111 | 0.90 | 38 | 18 | 25 | 12 |
| 68 | 0.4 | 630 | 168 | 0.90 | 60 | 29 | 40 | 20 |
| 69 | 0.4 | 630 | 81 | 0.90 | 92 | 44 | 61 | 30 |
| 70 | 0.4 | 630 | 174 | 0.90 | 44 | 21 | 30 | 14 |
| 71 | 0.4 | 400 | 118 | 0.92 | 94 | 46 | 63 | 31 |
| 72 | 0.4 | 250 | 69 | 0.90 | 36 | 21 | 24 | 14 |
| 73 | 0.4 | 250 | 69 | 0.89 | 200 | 37 | 25 | 13 |

3.1.1 the medium & low tension voltages

| Transformer number | Medium voltage(rated) kv | Medium voltage(actual) kv | Low voltage(rated) kv | Low voltage(actual) kv |
| --- | --- | --- | --- | --- |
| 1 | 33 | 33 | 0.4 | 0.398 |
| 2 | 33 | 32.941 | 0.4 | 0.398 |
| 3 | 33 | 32.826 | 0.4 | 0.396 |
| 4 | 33 | 32.74 | 0.4 | 0.395 |
| 5 | 33 | 32.711 | 0.4 | 0.395 |
| 6 | 33 | 32.706 | 0.4 | 0.396 |
| 7 | 33 | 32.687 | 0.4 | 0.395 |
| 8 | 33 | 32.675 | 0.4 | 0.395 |
| 9 | 33 | 32.649 | 0.4 | 0.395 |
| 10 | 33 | 32.617 | 0.4 | 0.394 |
| 11 | 33 | 32.552 | 0.4 | 0.392 |
| 12 | 33 | 32.529 | 0.4 | 0.393 |
| 13 | 33 | 32.472 | 0.4 | 0.392 |
| 14 | 33 | 32.787 | 0.4 | 0.392 |
| 15 | 33 | 32.772 | 0.4 | 0.392 |
| 16 | 33 | 32.77 | 0.4 | 0.393 |
| 17 | 33 | 32.769 | 0.4 | 0.392 |
| 18 | 33 | 32.764 | 0.4 | 0.392 |
| 19 | 33 | 32.764 | 0.4 | 0.392 |
| 20 | 33 | 32.763 | 0.4 | 0.392 |
| 21 | 33 | 32.763 | 0.4 | 0.393 |
| 22 | 33 | 32.82 | 0.4 | 0.393 |
| 23 | 33 | 32.721 | 0.4 | 0.391 |
| 24 | 33 | 32.695 | 0.4 | 0.391 |
| 25 | 33 | 32.69 | 0.4 | 0.392 |
| 26 | 33 | 32.624 | 0.4 | 0.392 |
| 27 | 33 | 32.614 | 0.4 | 0.391 |
| 28 | 33 | 32.571 | 0.4 | 0.391 |
| 29 | 33 | 32.536 | 0.4 | 0.391 |
| 30 | 33 | 32.516 | 0.4 | 0.391 |
| 31 | 33 | 32.515 | 0.4 | 0.390 |
| 32 | 33 | 32.524 | 0.4 | 0.391 |
| 33 | 33 | 32.524 | 0.4 | 0.391 |
| 34 | 33 | 32.521 | 0.4 | 0.391 |
| 35 | 33 | 32.515 | 0.4 | 0.390 |
| 36 | 33 | 32.512 | 0.4 | 0.391 |
| 37 | 33 | 32.507 | 0.4 | 0.390 |
| 38 | 33 | 32.506 | 0.4 | 0.391 |
| 39 | 33 | 32.635 | 0.4 | 0.391 |
| 40 | 33 | 32.631 | 0.4 | 0.391 |
| 41 | 33 | 32.611 | 0.4 | 0.391 |
| 42 | 33 | 32.578 | 0.4 | 0.391 |
| 43 | 33 | 32.569 | 0.4 | 0.391 |
| 44 | 33 | 32.564 | 0.4 | 0.391 |
| 45 | 33 | 32.566 | 0.4 | 0.391 |
| 46 | 33 | 32.559 | 0.4 | 0.391 |
| 47 | 33 | 32.552 | 0.4 | 0.391 |
| 48 | 33 | 32.548 | 0.4 | 0.391 |
| 49 | 33 | 32.662 | 0.4 | 0.391 |
| 50 | 33 | 32.658 | 0.4 | 0.391 |
| 51 | 33 | 32.656 | 0.4 | 0.392 |
| 52 | 33 | 32.305 | 0.4 | 0.395 |
| 53 | 33 | 32.304 | 0.4 | 0.395 |
| 54 | 33 | 32.242 | 0.4 | 0.395 |
| 55 | 33 | 32.231 | 0.4 | 0.394 |
| 56 | 33 | 32.231 | 0.4 | 0.394 |
| 57 | 33 | 32.226 | 0.4 | 0.395 |
| 58 | 33 | 32.222 | 0.4 | 0.395 |
| 59 | 33 | 32.219 | 0.4 | 0.394 |
| 60 | 33 | 32.218 | 0.4 | 0.394 |
| 61 | 33 | 32.233 | 0.4 | 0.394 |
| 62 | 33 | 32.201 | 0.4 | 0.394 |
| 63 | 33 | 32.181 | 0.4 | 0.394 |
| 64 | 33 | 32.178 | 0.4 | 0.394 |
| 65 | 33 | 32.176 | 0.4 | 0.394 |
| 66 | 33 | 32.178 | 0.4 | 0.394 |
| 67 | 33 | 32.176 | 0.4 | 0.394 |
| 68 | 33 | 32.174 | 0.4 | 0.394 |
| 69 | 33 | 32.168 | 0.4 | 0.395 |
| 70 | 33 | 32.165 | 0.4 | 0.394 |
| 71 | 33 | 32.611 | 0.4 | 0.391 |
| 72 | 33 | 32.55 | 0.4 | 0.391 |
| 73 | 33 | 32.768 | 0.4 | 0.392 |

The power factor on some transformers is low and we aim to rise both the power factor more than 0.92 and voltages to reach 100% nearly.

.

3.1.2 summary

we have to summarize the results, total generation, demand , loading., percentage of losses, and the total power factor.

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 4.927 | 2.348 | 5.457 | 90.3 lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 4.927 | 2.348 | 5.457 | 90.3 lag |
| Total Motor Load: | 2.940 | 1.363 | 3.241 | 90.7 lag |
| Total Static Load: | 1.920 | 0.890 |  |  |
| Apparent Losses: | 0.066 | 0.094 |  |  |

The swing current = 95A

3.2 the minimum load improvement

The minmum case after improvement using tap:3.2.1

| Transformer number | Rated kv | Actual kv | Tap % |
| --- | --- | --- | --- |
| 1 | 0.4 | 0.418 | 5 |
| 2 | 0.4 | 0.418 | 5 |
| 3 | 0.4 | 0.416 | 5 |
| 4 | 0.4 | 0.415 | 5 |
| 5 | 0.4 | 0.415 | 5 |
| 6 | 0.4 | 0.415 | 5 |
| 7 | 0.4 | 0.414 | 5 |
| 8 | 0.4 | 0.414 | 5 |
| 9 | 0.4 | 0.414 | 5 |
| 10 | 0.4 | 0.414 | 5 |
| 11 | 0.4 | 0.411 | 5 |
| 12 | 0.4 | 0.412 | 5 |
| 13 | 0.4 | 0.411 | 5 |
| 14 | 0.4 | 0.411 | 5 |
| 15 | 0.4 | 0.411 | 5 |
| 16 | 0.4 | 0.412 | 5 |
| 17 | 0.4 | 0.412 | 5 |
| 18 | 0.4 | 0.411 | 5 |
| 19 | 0.4 | 0.411 | 5 |
| 20 | 0.4 | 0.411 | 5 |
| 21 | 0.4 | 0.412 | 5 |
| 22 | 0.4 | 0.412 | 5 |
| 23 | 0.4 | 0.410 | 5 |
| 24 | 0.4 | 0.411 | 5 |
| 25 | 0.4 | 0.411 | 5 |
| 26 | 0.4 | 0.411 | 5 |
| 27 | 0.4 | 0.410 | 5 |
| 28 | 0.4 | 0.410 | 5 |
| 29 | 0.4 | 0.410 | 5 |
| 30 | 0.4 | 0.410 | 5 |
| 31 | 0.4 | 0.409 | 5 |
| 32 | 0.4 | 0.410 | 5 |
| 33 | 0.4 | 0.410 | 5 |
| 34 | 0.4 | 0.410 | 5 |
| 35 | 0.4 | 0.409 | 5 |
| 36 | 0.4 | 0.410 | 5 |
| 37 | 0.4 | 0.410 | 5 |
| 38 | 0.4 | 0.410 | 5 |
| 39 | 0.4 | 0.410 | 5 |
| 40 | 0.4 | 0.410 | 5 |
| 41 | 0.4 | 0.410 | 5 |
| 42 | 0.4 | 0.410 | 5 |
| 43 | 0.4 | 0.410 | 5 |
| 44 | 0.4 | 0.410 | 5 |
| 45 | 0.4 | 0.410 | 5 |
| 46 | 0.4 | 0.411 | 5 |
| 47 | 0.4 | 0.410 | 5 |
| 48 | 0.4 | 0.410 | 5 |
| 49 | 0.4 | 0.410 | 5 |
| 50 | 0.4 | 0.411 | 5 |
| 51 | 0.4 | 0.411 | 5 |
| 52 | 0.4 | 0.414 | 5 |
| 53 | 0.4 | 0.414 | 5 |
| 54 | 0.4 | 0.414 | 5 |
| 55 | 0.4 | 0.414 | 5 |
| 56 | 0.4 | 0.414 | 5 |
| 57 | 0.4 | 0.414 | 5 |
| 58 | 0.4 | 0.414 | 5 |
| 59 | 0.4 | 0.414 | 5 |
| 60 | 0.4 | 0.414 | 5 |
| 61 | 0.4 | 0.414 | 5 |
| 62 | 0.4 | 0.414 | 5 |
| 63 | 0.4 | 0.414 | 5 |
| 64 | 0.4 | 0.414 | 5 |
| 65 | 0.4 | 0.413 | 5 |
| 66 | 0.4 | 0.414 | 5 |
| 67 | 0.4 | 0.414 | 5 |
| 68 | 0.4 | 0.414 | 5 |
| 69 | 0.4 | 0.414 | 5 |
| 70 | 0.4 | 0.414 | 5 |
| 71 | 0.4 | 0.410 | 5 |
| 72 | 0.4 | 0.410 | 5 |
| 73 | 0.4 | 0.411 | 5 |

we have to summarize the results, total generation, demand , loading., percentage of losses, and the total power factor.

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 5.126 | 2.445 | 5.679 | 90.3 lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 5.126 | 2.445 | 5.679 | 90.3 lag |
| Total Motor Load: | 2.940 | 1.363 | 3.241 | 90.7 lag |
| Total Static Load: | 2.113 | 0.980 |  |  |
| Apparent Losses: | 0.072 | 0.102 |  |  |

The swing current = 99 A

3.2.2 Power factor improvement

Qc  = P(tan cos (p.f old)- tan cos (p.f new))

PF old = 90.3

PF new at least = 92%

Q=11.873 (tan (25.445) – tan(23.074)) = 255 KVAR

The capacitor is added in delta connection parallel to the transformer in secendary side(0.4 kv).

The table below shows the voltage level before and after adding  the capacitance:

| Transformer number | KVAR | Voltage before Add. cap | Voltage after Add. cap |
| --- | --- | --- | --- |
| 1 |  | 0.418 | 0.418 |
| 2 |  | 0.418 | 0.418 |
| 3 |  | 0.416 | 0.416 |
| 4 |  | 0.415 | 0.415 |
| 5 |  | 0.415 | 0.415 |
| 6 |  | 0.415 | 0.415 |
| 7 |  | 0.414 | 0.414 |
| 8 |  | 0.414 | 0.414 |
| 9 |  | 0.414 | 0.414 |
| 10 |  | 0.414 | 0.414 |
| 11 |  | 0.411 | 0.411 |
| 12 |  | 0.412 | 0.412 |
| 13 |  | 0.411 | 0.411 |
| 14 |  | 0.411 | 0.411 |
| 15 |  | 0.411 | 0.411 |
| 16 |  | 0.412 | 0.412 |
| 17 |  | 0.412 | 0.412 |
| 18 |  | 0.411 | 0.411 |
| 19 |  | 0.411 | 0.411 |
| 20 | 15 | 0.411 | 0.412 |
| 21 | 15 | 0.412 | 0.413 |
| 22 |  | 0.412 | 0.412 |
| 23 | 30 | 0.410 | 0.412 |
| 24 |  | 0.411 | 0.411 |
| 25 |  | 0.411 | 0.411 |
| 26 |  | 0.411 | 0.411 |
| 27 |  | 0.410 | 0.410 |
| 28 |  | 0.410 | 0.410 |
| 29 |  | 0.410 | 0.410 |
| 30 |  | 0.410 | 0.410 |
| 31 |  | 0.409 | 0.409 |
| 32 |  | 0.410 | 0.410 |
| 33 |  | 0.410 | 0.410 |
| 34 | 15 | 0.410 | 0.410 |
| 35 | 15 | 0.409 | 0.410 |
| 36 |  | 0.410 | 0.410 |
| 37 |  | 0.410 | 0.410 |
| 38 |  | 0.410 | 0.410 |
| 39 |  | 0.410 | 0.410 |
| 40 |  | 0.410 | 0.410 |
| 41 |  | 0.410 | 0.410 |
| 42 |  | 0.410 | 0.410 |
| 43 |  | 0.410 | 0.410 |
| 44 |  | 0.410 | 0.410 |
| 45 |  | 0.410 | 0.410 |
| 46 |  | 0.411 | 0.411 |
| 47 |  | 0.410 | 0.410 |
| 48 |  | 0.410 | 0.410 |
| 49 |  | 0.410 | 0.410 |
| 50 |  | 0.411 | 0.411 |
| 51 |  | 0.411 | 0.411 |
| 52 |  | 0.414 | 0.414 |
| 53 |  | 0.414 | 0.414 |
| 54 |  | 0.414 | 0.414 |
| 55 |  | 0.414 | 0.414 |
| 56 |  | 0.414 | 0.414 |
| 57 |  | 0.414 | 0.414 |
| 58 |  | 0.414 | 0.414 |
| 59 |  | 0.414 | 0.414 |
| 60 |  | 0.414 | 0.414 |
| 61 |  | 0.414 | 0.414 |
| 62 |  | 0.414 | 0.414 |
| 63 |  | 0.414 | 0.414 |
| 64 |  | 0.414 | 0.414 |
| 65 | 25 | 0.413 | 0.415 |
| 66 | 15 | 0.414 | 0.414 |
| 67 | 20 | 0.414 | 0.414 |
| 68 | 30 | 0.414 | 0.414 |
| 69 | 20 | 0.414 | 0.415 |
| 70 | 30 | 0.414 | 0.415 |
| 71 |  | 0.410 | 0.410 |
| 72 |  | 0.410 | 0.410 |
| 73 | 20 | 0.411 | 0.412 |

Total capacitors = 250 kvar

we have to summarize the results, total generation, demand , loading., percentage of losses, and the total power factor.

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 5.126 | 2.177 | 5.569 | 92.0 lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 5.126 | 2.177 | 5.569 | 92.0 lag |
| Total Motor Load: | 2.940 | 1.363 | 3.241 | 90.7 lag |
| Total Static Load: | 2.117 | 0.715 |  |  |
| Apparent Losses: | 0.069 | 0.098 |  |  |

The swing current = 97 A

We note:

when we increase power factor the losses in the network decrease and the total current decrease .

Losses before p.f improvement = 0.072 Mw .

Losses after p.f improvement = 0.069 Mw .

Total current in origin case = 99 A

Total current after PF  improvement= 97 A

3.2.3 comparison between three case

1.   the origin case .

2.   power factor improvement  case .

3.   improvement  using tap changing.

| Transformer number | Voltage Orginal case | Voltage Improve By tap | Pf improvement case.. |
| --- | --- | --- | --- |
| 1 | 0.398 | 0.418 | 0.418 |
| 2 | 0.398 | 0.418 | 0.418 |
| 3 | 0.396 | 0.416 | 0.416 |
| 4 | 0.395 | 0.415 | 0.415 |
| 5 | 0.395 | 0.415 | 0.415 |
| 6 | 0.396 | 0.415 | 0.415 |
| 7 | 0.395 | 0.414 | 0.414 |
| 8 | 0.395 | 0.414 | 0.414 |
| 9 | 0.395 | 0.414 | 0.414 |
| 10 | 0.394 | 0.414 | 0.414 |
| 11 | 0.392 | 0.411 | 0.411 |
| 12 | 0.393 | 0.412 | 0.412 |
| 13 | 0.392 | 0.411 | 0.411 |
| 14 | 0.392 | 0.411 | 0.411 |
| 15 | 0.392 | 0.411 | 0.411 |
| 16 | 0.393 | 0.412 | 0.412 |
| 17 | 0.392 | 0.412 | 0.412 |
| 18 | 0.392 | 0.411 | 0.411 |
| 19 | 0.392 | 0.411 | 0.411 |
| 20 | 0.392 | 0.411 | 0.412 |
| 21 | 0.393 | 0.412 | 0.413 |
| 22 | 0.393 | 0.412 | 0.412 |
| 23 | 0.391 | 0.410 | 0.412 |
| 24 | 0.391 | 0.411 | 0.411 |
| 25 | 0.392 | 0.411 | 0.411 |
| 26 | 0.392 | 0.411 | 0.411 |
| 27 | 0.391 | 0.410 | 0.410 |
| 28 | 0.391 | 0.410 | 0.410 |
| 29 | 0.391 | 0.410 | 0.410 |
| 30 | 0.391 | 0.410 | 0.410 |
| 31 | 0.390 | 0.409 | 0.409 |
| 32 | 0.391 | 0.410 | 0.410 |
| 33 | 0.391 | 0.410 | 0.410 |
| 34 | 0.391 | 0.410 | 0.410 |
| 35 | 0.390 | 0.409 | 0.410 |
| 36 | 0.391 | 0.410 | 0.410 |
| 37 | 0.390 | 0.410 | 0.410 |
| 38 | 0.391 | 0.410 | 0.410 |
| 39 | 0.391 | 0.410 | 0.410 |
| 40 | 0.391 | 0.410 | 0.410 |
| 41 | 0.391 | 0.410 | 0.410 |
| 42 | 0.391 | 0.410 | 0.410 |
| 43 | 0.391 | 0.410 | 0.410 |
| 44 | 0.391 | 0.410 | 0.410 |
| 45 | 0.391 | 0.410 | 0.410 |
| 46 | 0.391 | 0.411 | 0.411 |
| 47 | 0.391 | 0.410 | 0.410 |
| 48 | 0.391 | 0.410 | 0.410 |
| 49 | 0.391 | 0.410 | 0.410 |
| 50 | 0.391 | 0.411 | 0.411 |
| 51 | 0.392 | 0.411 | 0.411 |
| 52 | 0.395 | 0.414 | 0.414 |
| 53 | 0.395 | 0.414 | 0.414 |
| 54 | 0.395 | 0.414 | 0.414 |
| 55 | 0.394 | 0.414 | 0.414 |
| 56 | 0.394 | 0.414 | 0.414 |
| 57 | 0.395 | 0.414 | 0.414 |
| 58 | 0.395 | 0.414 | 0.414 |
| 59 | 0.394 | 0.414 | 0.414 |
| 60 | 0.394 | 0.414 | 0.414 |
| 61 | 0.394 | 0.414 | 0.414 |
| 62 | 0.394 | 0.414 | 0.414 |
| 63 | 0.394 | 0.414 | 0.414 |
| 64 | 0.394 | 0.414 | 0.414 |
| 65 | 0.394 | 0.413 | 0.415 |
| 66 | 0.394 | 0.414 | 0.414 |
| 67 | 0.394 | 0.414 | 0.414 |
| 68 | 0.394 | 0.414 | 0.414 |
| 69 | 0.395 | 0.414 | 0.415 |
| 70 | 0.394 | 0.414 | 0.415 |
| 71 | 0.391 | 0.410 | 0.410 |
| 72 | 0.391 | 0.410 | 0.410 |
| 73 | 0.392 | 0.411 | 0.412 |

3.2.4 voltage level improvement using capacitors:

| Transformer number | voltage(rated) kv | Q(KVAR) | voltage(actual) before add. capacitors | voltage(rated) after add. capacitors | Pf before | Pf after |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.4 | 10 | 0.398 | 0.399 | 79 | 96 |
| 2 | 0.4 | 20 | 0.398 | 0.399 | 90 | 98 |
| 3 | 0.4 | 10 | 0.396 | 0.397 | 88 | 98 |
| 4 | 0.4 |  | 0.395 |  | 93 |  |
| 5 | 0.4 |  | 0.395 |  | 92 |  |
| 6 | 0.4 |  | 0.396 |  | 99 |  |
| 7 | 0.4 |  | 0.395 |  | 92 |  |
| 8 | 0.4 |  | 0.395 |  | 95 |  |
| 9 | 0.4 |  | 0.395 |  | 93 |  |
| 10 | 0.4 |  | 0.394 |  | 93 |  |
| 11 | 0.4 | 80 | 0.392 | 0.394 | 70 | 99 |
| 12 | 0.4 | 30 | 0.393 | 0.394 | 89 | 97 |
| 13 | 0.4 | 30 | 0.392 | 0.393 | 90 | 98 |
| 14 | 0.4 | 30 | 0.392 | 0.393 | 88 | 99 |
| 15 | 0.4 | 30 | 0.392 | 0.393 | 86 | 99 |
| 16 | 0.4 |  | 0.393 |  | 98 |  |
| 17 | 0.4 | 15 | 0.392 | 0.393 | 88 | 98 |
| 18 | 0.4 | 20 | 0.392 | 0.393 | 86 | 97 |
| 19 | 0.4 | 20 | 0.392 | 0.393 | 91 | 99 |
| 20 | 0.4 | 20 | 0.392 | 0.393 | 88 | 97 |
| 21 | 0.4 | 15 | 0.393 | 0.393 | 89 | 98 |
| 22 | 0.4 |  | 0.393 |  | 88 |  |
| 23 | 0.4 | 30 | 0.391 | 0.393 | 76 | 96 |
| 24 | 0.4 |  | 0.391 |  | 93 |  |
| 25 | 0.4 |  | 0.392 |  | 92 |  |
| 26 | 0.4 |  | 0.392 |  | 98 |  |
| 27 | 0.4 | 40 | 0.391 | 0.392 | 83 | 96 |
| 28 | 0.4 |  | 0.391 |  | 94 |  |
| 29 | 0.4 |  | 0.391 |  | 94 |  |
| 30 | 0.4 | 20 | 0.391 | 0.392 | 90 | 98 |
| 31 | 0.4 | 20 | 0.390 | 0.391 | 90 | 94 |
| 32 | 0.4 |  | 0.391 |  | 91 |  |
| 33 | 0.4 |  | 0.391 |  | 92 |  |
| 34 | 0.4 | 30 | 0.391 | 0.392 | 87 | 97 |
| 35 | 0.4 | 30 | 0.390 | 0.391 | 90 | 98 |
| 36 | 0.4 | 10 | 0.391 | 0.392 | 91 | 99 |
| 37 | 0.4 | 20 | 0.390 | 0.392 | 90 | 96 |
| 38 | 0.4 | 10 | 0.391 | 0.392 | 90 | 99 |
| 39 | 0.4 | 15 | 0.391 | 0.393 | 74 | 98 |
| 40 | 0.4 | 15 | 0.391 | 0.393 | 78 | 98 |
| 41 | 0.4 | 15 | 0.391 | 0.392 | 91 | 95 |
| 42 | 0.4 |  | 0.391 |  | 94 |  |
| 43 | 0.4 |  | 0.391 |  | 96 |  |
| 44 | 0.4 | 30 | 0.391 | 0.392 | 91 | 98 |
| 45 | 0.4 |  | 0.391 |  | 94 |  |
| 46 | 0.4 |  | 0.391 |  | 94 |  |
| 47 | 0.4 | 15 | 0.391 | 0.392 | 90 | 96 |
| 48 | 0.4 | 15 | 0.391 | 0.393 | 90 | 99 |
| 49 | 0.4 | 10 | 0.391 | 0.393 | 88 | 99 |
| 50 | 0.4 | 15 | 0.391 | 0.393 | 92 | 98 |
| 51 | 0.4 |  | 0.392 |  | 96 |  |
| 52 | 0.4 | 15 | 0.395 | 0.396 | 90 | 95 |
| 53 | 0.4 | 15 | 0.395 | 0.396 | 92 | 98 |
| 54 | 0.4 | 15 | 0.395 | 0.395 | 92 | 95 |
| 55 | 0.4 |  | 0.394 |  | 94 |  |
| 56 | 0.4 | 15 | 0.394 | 0.395 | 90 | 97 |
| 57 | 0.4 |  | 0.395 |  | 95 |  |
| 58 | 0.4 |  | 0.395 |  | 94 |  |
| 59 | 0.4 | 20 | 0.394 | 0.395 | 90 | 98 |
| 60 | 0.4 | 20 | 0.394 | 0.395 | 90 | 98 |
| 61 | 0.4 |  | 0.394 |  | 88 |  |
| 62 | 0.4 |  | 0.394 |  | 92 |  |
| 63 | 0.4 | 10 | 0.394 | 0.396 | 88 | 99 |
| 64 | 0.4 | 10 | 0.394 | 0.396 | 90 | 99 |
| 65 | 0.4 | 20 | 0.394 | 0.395 | 88 | 97 |
| 66 | 0.4 | 20 | 0.394 | 0.395 | 90 | 98 |
| 67 | 0.4 | 30 | 0.394 | 0.395 | 90 | 98 |
| 68 | 0.4 | 50 | 0.394 | 0.395 | 90 | 98 |
| 69 | 0.4 | 30 | 0.395 | 0.396 | 90 | 99 |
| 70 | 0.4 | 50 | 0.394 | 0.395 | 90 | 98 |
| 71 | 0.4 | 15 | 0.391 | 0.392 | 92 | 95 |
| 72 | 0.4 | 20 | 0.391 | 0.392 | 90 | 98 |
| 73 | 0.4 | 20 | 0.392 | 0.393 | 89 | 98 |

The result of basic information of the network after adding capacitance:

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 4.931 | 1.328 | 5.106 | 96.6 lag |
| Generators: | 0.000 | 0.000 | 0.000 | 100.00 lag |
| Total Demand: | 4.931 | 1.328 | 5.106 | 96.6 lag |
| Total Motor Load: | 2.940 | 1.363 | 3.241 | 90.7 lag |
| Total Static Load: | 1.932 | 0.069 |  |  |
| Apparent Losses: | 0.058 | 0.082 |  |  |

Chapter four:

Two connection point

SUMMARY OF TOTAL GENERATION, LOADING & DEMAND

|  | MW | Mvar | MVA | % PF |
| --- | --- | --- | --- | --- |
| Swing Bus(es): | 2.299 | 2.166 | 3.158 | 72.8lag |
| Generators: | 10.00 | 4.300 | 10.885 | 91.9 lag |
| Total Demand: | 2.299 | 6.466 | 13.895 | 88.5lag |
| Total Motor Load: | 4.932 | 2.288 | 5.437 | 90.7 lag |
| Total Static Load: | 6.980 | 3.231 |  |  |
| Apparent Losses: | 0.387 | 0.947 |  |  |

Comparison between two case

1.one connection point

2.two connection point

| Transformer number | Rated voltage (KV) | Actual voltag with One connection point | Actual voltag with two connection point |
| --- | --- | --- | --- |
| 1 | 0.4 | 0.386 | 0.386 |
| 2 | 0.4 | 0.386 | 0.387 |
| 3 | 0.4 | 0.381 | 0.385 |
| 4 | 0.4 | 0.380 | 0.386 |
| 5 | 0.4 | 0.380 | 0.387 |
| 6 | 0.4 | 0.383 | 0.390 |
| 7 | 0.4 | 0.378 | 0.386 |
| 8 | 0.4 | 0.379 | 0.387 |
| 9 | 0.4 | 0.380 | 0.389 |
| 10 | 0.4 | 0.379 | 0.389 |
| 11 | 0.4 | 0.368 | 0.381 |
| 12 | 0.4 | 0.373 | 0.387 |
| 13 | 0.4 | 0.372 | 0.388 |
| 14 | 0.4 | 0.370 | 0.385 |
| 15 | 0.4 | 0.370 | 0.386 |
| 16 | 0.4 | 0.377 | 0.392 |
| 17 | 0.4 | 0.375 | 0.390 |
| 18 | 0.4 | 0.371 | 0.387 |
| 19 | 0.4 | 0.372 | 0.387 |
| 20 | 0.4 | 0.370 | 0.386 |
| 21 | 0.4 | 0.378 | 0.394 |
| 22 | 0.4 | 0.379 | 0.395 |
| 23 | 0.4 | 0.367 | 0.385 |
| 24 | 0.4 | 0.370 | 0.389 |
| 25 | 0.4 | 0.372 | 0.391 |
| 26 | 0.4 | 0.373 | 0.395 |
| 27 | 0.4 | 0.366 | 0.390 |
| 28 | 0.4 | 0.371 | 0.398 |
| 29 | 0.4 | 0.370 | 0.4 |
| 30 | 0.4 | 0.368 | 0.401 |
| 31 | 0.4 | 0.363 | 0.396 |
| 32 | 0.4 | 0.369 | 0.399 |
| 33 | 0.4 | 0.369 | 0.4 |
| 34 | 0.4 | 0.369 | 0.399 |
| 35 | 0.4 | 0.366 | 0.399 |
| 36 | 0.4 | 0.369 | 0.391 |
| 37 | 0.4 | 0.368 | 0.399 |
| 38 | 0.4 | 0.380 | 0.398 |
| 39 | 0.4 | 0.366 | 0.4 |
| 40 | 0.4 | 0.365 | 0.385 |
| 41 | 0.4 | 0.369 | 0.384 |
| 42 | 0.4 | 0.370 | 0.388 |
| 43 | 0.4 | 0.371 | 0.389 |
| 44 | 0.4 | 0.369 | 0.390 |
| 45 | 0.4 | 0.371 | 0.388 |
| 46 | 0.4 | 0.374 | 0.389 |
| 47 | 0.4 | 0.369 | 0.392 |
| 48 | 0.4 | 0.370 | 0.388 |
| 49 | 0.4 | 0.370 | 0.389 |
| 50 | 0.4 | 0.371 | 0.388 |
| 51 | 0.4 | 0.373 | 0.390 |
| 52 | 0.4 | 0.379 | 0.392 |
| 53 | 0.4 | 0.379 | 0.385 |
| 54 | 0.4 | 0.379 | 0.386 |
| 55 | 0.4 | 0.378 | 0.386 |
| 56 | 0.4 | 0.378 | 0.385 |
| 57 | 0.4 | 0.381 | 0.384 |
| 58 | 0.4 | 0.379 | 0.388 |
| 59 | 0.4 | 0.378 | 0.386 |
| 60 | 0.4 | 0.378 | 0.384 |
| 61 | 0.4 | 0.377 | 0.384 |
| 62 | 0.4 | 0.378 | 0.384 |
| 63 | 0.4 | 0.378 | 0.385 |
| 64 | 0.4 | 0.378 | 0.385 |
| 65 | 0.4 | 0.376 | 0.385 |
| 66 | 0.4 | 0.377 | 0.383 |
| 67 | 0.4 | 0.377 | 0.384 |
| 68 | 0.4 | 0.377 | 0.384 |
| 69 | 0.4 | 0.383 | 0.384 |
| 70 | 0.4 | 0.377 | 0.390 |
| 71 | 0.4 | 0.369 | 0.384 |
| 72 | 0.4 | 0.369 | 0.388 |
| 73 | 0.4 | 0.371 | 0.388 |

We notes

Losses before = 0.421 MW

Losses after =0.387 MW

Chapter five:

Economical Study

_Pmax=13.215 mw

_Pmin=5.126mw

_Losses before improvement =0.485mw

_Losses after improvement =0.46mw

_(Pf )before improvement in max. case=0.895

_(Pf) before imrovement in min. case=0.905

_(Pf) after improvement=0.92

To find the economical operation of the network we must do the the following calculation:

Pav=(Pmax+Pmin)/2=(13.215+5.126)/2=9.1705mw

LF=Pav/Pmax=0.7

Total energy per year=Pmax*LF*total hour per year

=13.215*0.7*8760=80333.58*10^3 KWH

Total cost per year=total energy*cost(NIS/KWH)

=80333.58*10^3*0.33=26510.08*10^3NIS/YEAR

Saving in penalites of( PF): Table below show relation of PF to the penalties :

| PF | Penalties |
| --- | --- |
| 0.92 or more | No penalties |
| Less than 0.92 to 0.8 | 1%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.8 to 0.7 | 1.25%of the total bill for every 0.01 of PF less than 0.92 |
| Less than 0.7 | 1.5%of the total bill for every 0.01 of PF less than 0.92 |

Penalites=0.01*(0.92-pf)*total bill

=0.01*0.02*26510.08*10^3=5300 NIS/YEAR

Cost of losses:

Losses before improvement=0.485*0.7=339.5kw

Energy=339.5*8760=2974.02*10^3 kwh

Total cost=2974.02*10^3*0.33=981426 NIS/YEAR

Losses after improvement=460*0.7=322kw

Energy=2820.72kwh

Cost of losses=2820.72*0.33=930837NIS/YEAR

Saving in cost of losses=cost beforeimprovement-cost after improvement

=50859 NIS/YEAR

Total capacitor =957kvar

(Cost per KVAR)with control circuit=15 JD=75NIS

Total cost of capacitors=957*75=71775NIS

Total saving=saving in penalites+ saving in losses

=5300+50589=55889

S.P.B.P=(investment)/(saving)

=71775/55889=1.28 YEAR.