Najah National University

Faculty of Electrical engineering

Introduction to Graduation Project

"Techno-economic feasibility of using photovoltaic generators instead of diesel motor for water pumping"

Supervisors:

Prof. Dr.Marwan M. Mahmud

:	Prepared by

Sabreen Staiti

Heba Aseedah

Yasmeen Salah

Table of contents

| content | page |
| --- | --- |
| Chapter 1 introduction | 2 |
| Chapter 2 The content of pv and diesel systems | 4-6 |
| Chapter 3 The data of well needed | 7-14 |
| Chapter 4 The calculation of wells capital cost for pv and diesel systems | 15-34 |
| Chapter 5 The calculation of average value of yearly pumping water | 35-72 |
| Chapter 6 Economical evaluation of energy supply systems | 73-90 |
| Chapter 7 Net present value ( NPV ) | 91-95 |
| Chapter 8 Life cycle cost | 96-101 |
| Chapter 9 Breakeven point | 102 |

Introduction

In rural and/or undeveloped areas where there is no power grid and more water is needed than what hand or foot pumps can deliver, the choices for powering pumps are usually solar or a fuel driven engine, usually diesel .There are very distinct differences between the two power sources in terms of cost and reliability. Diesel a very high operation and maintenance cost. Solar is the opposite, with a higher first cost but very low on going operation and maintenance costs.

In terms of reliability, it is much easier (and cheaper) to keep a solar-powered system going than it is a diesel engine. This is evident in field where diesel engines lie rusting and unused by the thousands and solar pumps sometimes run for year without anyone touching them

The first cost of solar is often daunting to donors and project implementers who are tempted to stretch their budgets as far as possible to reach the greatest number of beneficiaries by using a low first-cost option. But most would probably agree that “quantity over quality” is not a good value if the higher quantity option is not likely to be giving good service five years down the road and if beneficiaries are going to be stuck with interventions they cannot afford to sustain over time.

Solar pumping has had clear advantages for a number of years but the differences are becoming more striking in a world of rapidly escalating fuel costs. Not only will some of the world’s poorest people not be able to afford fuel for their pumps, but living at the end of remote supply chains, they may not even be able to get it in the first place as world demand overtakes supply

Chapter 2

The content of photovoltaic and diesel water pumping system

2-1 Photovoltaic water pumping system

1- Solar radiation

2- Pv generator

3- Inverter

4- ASM

5- A centrifugal pump

6- Storage tank

Components of  Water pumping system driven by a diesel

h

S.G

ASM

M

Pump

Diesel

Motor

Three phase

Asyn G

Motor

Well

Storage

Tank

The component of pumping water by diesel:

1- Diesel motor.

2- Synchronous generator.

3- Three phase asynchronous motor.

4- Pump.

5- Storage tank.

Chapter 3

The data of well needed

The data of well needed for our project is:-

| اسم صاحب البئر | انس محمد نجيب مسا د |
| --- | --- |
| الهاتف | 0599477308 |
| العنوان | برقين |
| طبيعة الاستخدام | زراعي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 40 |
| 2. | مستوى الماء الثابت SWL | متر | 12 |
| 3. | مستوى الماء المتحرك DWL | متر | 35 |
| 4. | قطر مواسير التعليق | أنش | 2" بربيش |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 2.5 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 3 |

معلومات المضخة

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5.5 |
| 2. | عدد فازات المضخة | 3 فاز |

**********************************************************

| اسم صاحب البئر | احمد عبد الطيف عامودي |
| --- | --- |
| الهاتف | 0522412124 |
| العنوان | مثلث كفر قود |
| طبيعة الاستخدام | زراعي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 60 |
| 2. | مستوى الماء الثابت SWL | متر | 20 |
| 3. | مستوى الماء المتحرك DWL | متر | 56 |
| 4. | قطر مواسير التعليق | انش | 2" |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 3 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 12 |

معلومات المضخة :

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5 |
| 2. | عدد فازات المضخة | 3 فاز |

**********************************************************

| اسم صاحب البئر | جميل محمد نجيب مساد |
| --- | --- |
| الهاتف | 0522272029 |
| العنوان | برقين |
| طبيعة الاستخدام | زراعي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 45 |
| 2. | مستوى الماء الثابت SWL | متر | 12 |
| 3. | مستوى الماء المتحرك DWL | متر | 40 |
| 4. | قطر مواسير التعليق | انش | 2" بربيش |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 3 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 5 |

معلومات المضخة :

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5.5 |
| 2. | عدد فازات المضخة | 3 فاز |

**********************************************************

| اسم صاحب البئر | خليل مصطفى احمد غانم |
| --- | --- |
| الهاتف | 042501847 |
| العنوان | مثلث كفر قود |
| طبيعة الاستخدام | زراعي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 60 |
| 2. | مستوى الماء الثابت SWL | متر | 30 |
| 3. | مستوى الماء المتحرك DWL | متر | 50 |
| 4. | قطر مواسير التعليق | انش | 2" |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 4 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 12 |

معلومات المضخة :

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 7 |
| 3. | عدد فازات المضخة | 3 فاز |

******************************************************

| اسم صاحب البئر | رائد عويص |
| --- | --- |
| الهاتف | 0599970669 |
| العنوان | مثلث كفرقود |
| طبيعة الاستخدام | زراعي + منزلي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 70 |
| 2. | مستوى الماء الثابت SWL | متر | 20 |
| 3. | مستوى الماء المتحرك DWL | متر | 60 |
| 4. | قطر مواسير التعليق | انش | 2" |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 3 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 12 |

معلومات المضخة :

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5 |
| 2. | عدد فازات المضخة | 3 فاز |

| اسم صاحب البئر | كامل عمر ابراهيم عباس |
| --- | --- |
| الهاتف | 0599264086 |
| العنوان | برقين |
| طبيعة الاستخدام | زراعي |

معلومات البئر :

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 50 |
| 2. | مستوى الماء الثابت SWL | متر | 18 |
| 3. | مستوى الماء المتحرك DWL | متر | 32 |
| 4. | قطر مواسير التعليق | انش | 2" |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 12 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 24 صيفا |

معلومات المضخة :

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5.5 |
| 2. | عدد فازات المضخة | 3 فاز |

***************************************************************************

| اسم صاحب البئر | محمود عبد الطيف عامودي |
| --- | --- |
| الهاتف | 0522412124 |
| العنوان | مثلث كفر قود |
| طبيعة الاستخدام | زراعي |

معلومات البئر

| الرقم | البيان | الوحدة | الكمية |
| --- | --- | --- | --- |
| 1. | عمق البئر | متر | 70 |
| 2. | مستوى الماء الثابت SWL | متر | 30 |
| 3. | مستوى الماء المتحرك DWL | متر | 60 |
| 4. | قطر مواسير التعليق | انش | 2" |
| 5. | كمية المياه المنتجة خلال ساعة | م3/ساعة | 3 |
| 6. | معدل عدد ساعات الضخ يوميا | ساعة | 12 |

معلومات المضخة:

| الرقم | البيان | التوضيح |
| --- | --- | --- |
| 1. | قدرة المضخة hp | 5 |
| 2. | عدد فازات المضخة | 3 فاز |

Chapter 4

The calculation of wells capital cost for PV and diesel systems

4-1 The calculation of capital cost for pv system

رائد عويص

Well depth=70m.

Swl = 20m.

Dwl = 60m.

Pipe = 2inch.

Compute of the well = 3 m3/ hour       , 12 hour / day .

Total pumping head (ht) = 60 + (6m) = 66m.

Total water capacity needed per day =3 ×12=36 m3/ day

Eh =0.002725×V × hT

=0.002725×36 ×66= 6.47kwh / day

E p in  =11.76kwh /day .

E asm in  = 14.34 Kwh / day.

E inv in =15.42 kwh / day.

Psh =5.4 kwh /day.

1kwp       →5.4 kWh /day.

?       → 15.42 kWh / day.

PPV= 2.85 kwp.

PV   →   1 wp = 2.5 $

The cost of PV cells   : -      2850* 2.5 = 7125 $

Inverter cost = 1800 $

Motor pump set = 1000 $

Piping and accessories = 400 $

The capital cost =   7125 +1800+1000+400

=   10325 $

**********************************

جميل مساد

Well depth=45m.

Swl = 12m.

Dwl = 40m.

Pipe = 2inch.

Output of the well = 3 m3/ hour   for  5 hour / day .

Total pumping head (hT) = 40 +(6m) = 46m.

Total water capacity needed per day =3 ×5=15 m3

Eh =0.002725×V × hT

=0.002725×15×46= 1.88kwh / day

E p in  =3.42 kwh /day .

E ASM in  = 4.17 Kwh / day  .

E inv in = =4.48 kwh / day.

Psh =5.4 kwh /day.

1kwp       →5.4 kWh /day.

?       → 4.48 kwh / day.

PPV= .829 kwp .

The cost of Pv cells   :-      829* 2.5=2072.5 $

Inverter cost = 1400 $

Motor pump set = 800 $

Piping and accessories = 300 $

The capital cost =   2072.5 +1400 +800 +300

=   4572.5 $

********************************************************

خليل غانم

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2inch.

Output of the well = 4 m3/ hour   for  12 hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =4 ×12=48 m3

Eh =0.002725×V × hT

=0.002725×48×56= 7.32kwh / day

E p in  =13.3 kwh /day .

E ASM in  = 16.23 Kwh / day.

E inv in = =17.45 kWh / day.

Psh =5.4 kWh /day.

1kwp       →5.4 kWh /day.

?       → 17.45 kWh / day.

PPV= 3.23 kwp .

The cost of Pv cells   :-      3230 *2.5  =8075 $

Inverter cost = 2000 $

Motor pump set = 1200 $

Piping and accessories = 420 $

The capital cost = 8075 +2000 +120 =   11695 $

.**********************************************************

احمد عامودي

Well depth=60m.

Swl = 20m.

Dwl = 56m.

Pipe = 2inch.

Output of the well =   3 m3/ hour   for   12 hour / day .

Total pumping head   (h T) = 56 + (6m) = 62 m.

Total water capacity needed per day =3 ×12=36 m3

Eh =0.002725×V × h T

=0.002725×36×62= 6.08kwh / day

E p in   =11.05 k w h /day .

E ASM in  = 13.48   K w h / day   .

E inv in = =14.49 k w h / day.

P sh =5.4 k w h /day.

1kwp       →5.4 kWh /day.

?       → 14.49 kWh / day.

PPV= 2.68 kwp.

.

The cost of Pv cells   :-      2068*2.5  =5170 $

Inverter cost = 1800 $

Motor pump set = 1000 $

Piping and accessories = 400 $

The capital cost = 1800 +1000 +400 +5170

=   8370 $

.**********************************************************

أنس مساد  .

Well depth=40m

Swl = 12m.

Dwl = 35m.

Pipe = 2inch.

Output of the well =   2.5 m3/ hour   for   3 hour / day .

Total pumping head   (h T) = 35 + (6m) = 41 m.

Total water capacity needed per day =2.5 ×3=7.5 m3/ day .

Eh =0.002725×V × h T

=0.002725×7.5×41= 0.84kwh / day

E p in   =1. 53 k w h /day .

E ASM in  = 1 .86  K w h / day   .

E inv in = =2 k w h / day  .

P sh =5.4 k w h /day.

1kwp       →5.4 kwh /day.

?       → 2 kwh / day.

PPV= .37 kwp .

The cost of Pv cells   :-      370 * 2.5 =925 $

Inverter cost = 1300 $

Motor pump set = 700 $

Piping and accessories = 300 $

The capital cost = 925 +1300 +700 +300

=   3225 $

.**********************************************************

محمود العامودي

Well depth=70m

Swl = 30m.

Dwl = 60m.

Pipe = 2inch.

Output of the well =   3 m3/ hour   for   12 hour / day .

Total pumping head   (h T) = 60 + (6m) = 66 m.

Total water capacity needed per day =12 ×3=36 m3/ day .

Eh =0.002725×V × h T

=0.002725×36×66= 6.47 kwh / day

E p in   =11. 76 k w h /day .

E ASM in  = 14 .34  K w h / day   .

E inv in = =15.42 k w h / day  .

P sh =5.4 k w h /day.

1kwp       →5.4 kwh /day.

?       → 15.42 kwh / day.

PPV= 2.86 kwp .

The cost of Pv cells   :-     2860 * 2.5 =7150 $

Inverter cost = 1800 $

Motor  pump set = 1000 $

Piping  and accessories = 400 $

The capital  cost = 7150 +1800 +1000 +400

=   30350 $

******************************************************

كامل عمر ابراهيم عباس

Well depth=50 m

Swl = 18 m.

Dwl = 32m.

Pipe = 2 inch.

Output of the well =   50 m3/ hour   for   4 hour / day .

Total pumping head   (h T) = 32 + (6m) = 38 m.

Total water capacity needed per day =50 ×4=200 m3/ day .

Eh =0.002725×V × h T

=0.002725×200×38= 20.71 kwh / day

E p in   =20.710/ .55 = 37.65 k w h /day .

E ASM in =37.65 / .82 = 45.9  K w h / day   .

E inv in =45.9 / .92 =49.37 k w h / day  .

P sh =5.4 k w h /day.

1kwp       →5.4 kwh /day.

?       → 49.3 kwh / day.

PPV= 9.14 kwp .

The cost of Pv cells   :-     9140 * 2.5 =22850 $

Inverter cost = 4500$

Motor  pump set = 2000 $

Piping  and accessories = 500 $

The capital  cost = 22850 +4500 +2000 +500

=   29850 $

| Capital cost | Hydroulic energy | wells |
| --- | --- | --- |
| 10325 $ | 6.47kwh / day | رائد عويص Well depth=70m . 63 m3/ day |
| 4572.5 $ | 1.88kwh / day | جميل مساد Well depth=45m . 15 m3/ day |
| 11695 $ | 7.32kwh / day | خليل غانم Well depth=60m . 48 m3/ day |
| 8370 $ | 6.08kwh / day | احمد عامودي Well depth=60m .36 m3/ day |
| 3225 $ | 0.84kwh / day | أنس مساد Well depth=40m . 7.5 m3/ day |
| 30350 $ | 6.47 kwh / day | محمود العامودي Well depth=70m . 36 m3/ day |
| 29850 $ | 20.71 kwh / day | كامل عمر ابراهيم عباس Well depth=50m . 200 m3/ day |

4-2 the calculation of capital cost for diesel system

رائد عويص

Well depth=70m.

Swl = 20m.

Dwl = 60m.

Pipe = 2inch.

Compute of the well =  3 m3/ hour       ,12 hour / day .

Total pumping head  (hT  ) = 60 +(6m) = 66m.

Total water capacity needed per day =3 ×12=36 m3

Eh =0.002725×V × hT

=0.002725×36 ×66= 6.47kwh / day

E p in  =11.76kwh /day .

E ASM in  = 14.34 Kwh / day  .

E S.G in   = 14.34/0.75 = 19.12 kwh

E DIESEL in =19.12/0.30 = 63.7 kwh

Number of liters diesel needed daily = 63.7/10.5 = 6

Diesel cost = 6* 6 NIS =36 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 1000 $

Piping  and accessories = 400 $

Capital cost = 4525 $

*******************************************************

جميل مساد

Well depth=45m.

Swl = 12m.

Dwl = 40m.

Pipe = 2inch.

Output of the well =  3 m3/ hour   for  5 hour / day .

Total pumping head  (hT) = 40 +(6m) = 46m.

Total water capacity needed per day =3 ×5=15 m3

Eh =0.002725×V × hT

=0.002725×15×46= 1.88kwh / day

E p in  =3.42 kwh /day .

E ASM in  = 4.17  Kwh / day  .

E S.G in   = 4.17/0.75 = 5.56 kwh

E DIESEL in =5.56/0.30 = 18.53 kwh

Number of liters diesel needed daily = 18.53/10.5 = 1.76

Diesel cost = 6* 6 NIS =10.56 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 800 $

Piping  and accessories = 300 $

Capital cost = 4225 $

***************************************************

خليل غانم

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2inch.

Output of the well =  4 m3/ hour   for  12 hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =4 ×12=48 m3

Eh =0.002725×V × hT

=0.002725×48×56= 7.32kwh / day

E p in  =13.3 kwh /day .

E ASM in  = 16.23  Kwh / day  .

E S.G in   = 16.23/0.75 = 21.64 kwh

E DIESEL in =21.64/0.30 = 72.13 kwh

Number of liters diesel needed daily = 72.13/10.5 = 6.87

Diesel cost = 6* 6.87 NIS =41.22NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 1200 $

Piping  and accessories = 420 $

Capital cost = 4745 $

احمد عامودي

Well depth=60m.

Swl = 20m.

Dwl = 56m.

Pipe = 2inch.

Output of the well =   3 m3/ hour   for   12 hour / day .

Total pumping head   (h T) = 56 + (6m) = 62 m.

Total water capacity needed per day =3 ×12=36 m3

Eh =0.002725×V × h T

=0.002725×36×62= 6.08kwh / day

E p in   =11.05 k w h /day .

E ASM in  = 13.48   K w h / day   .

E S.G in   = 13.48/0.75 = 17.97 kwh

E DIESEL in =17.97/0.30 = 59.9 kwh

Number of liters diesel needed daily = 59.9/10.5 = 5.7

Diesel cost = 6* 5.7 NIS =34.2 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 1000 $

Piping  and accessories = 400 $

Capital cost = 4525 $

**************************************************

أنس مساد  .

Well depth=40m

Swl = 12m.

Dwl = 35m.

Pipe = 2inch.

Output of the well =   2.5 m3/ hour   for   3 hour / day .

Total pumping head   (h T) = 35 + (6m) = 41 m.

Total water capacity needed per day =2.5 ×3=7.5 m3/ day .

Eh =0.002725×V × h T

=0.002725×7.5×41= 0.84kwh / day

E p in   =1. 53 k w h /day .

E ASM in  = 1 .86  K w h / day   .

E S.G in   = 1.86/0.75 = 2.48 kwh

E DIESEL in =2.48/0.30 = 8.2 kwh

Number of liters diesel needed daily = 8.2/10.5 =.78

Diesel cost = 6* .78 NIS =4.68 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 700 $

Piping  and accessories = 300 $

Capital cost = 4125 $

*******************************************************

محمود العامودي

Well depth=70m

Swl = 30m.

Dwl = 60m.

Pipe = 2inch.

Output of the well =   3 m3/ hour   for   12 hour / day .

Total pumping head   (h T) = 60 + (6m) = 66 m.

Total water capacity needed per day =12 ×3=36 m3/ day .

Eh =0.002725×V × h T

=0.002725×36×66= 6.47 kwh / day

E p in   =11. 76 k w h /day .

E ASM in  = 14 .34  K w h / day   .

E S.G in   = 14.34/0.75 = 19.12 kwh

E DIESEL in =19.12/0.30 = 63.73 kwh

Number of liters diesel needed daily = 63.73/10.5 =6.06

Diesel cost = 6* 6.06 NIS =36.36 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 1000 $

Piping  and accessories = 400 $

Capital cost = 4525 $

.*********************************************************

كامل عمر ابراهيم عباس

Well depth=50m

Swl = 18m.

Dwl = 32m.

Pipe = 2inch.

Output of the well =   50 m3/ hour   for   4 hour / day .

Total pumping head   (h T) = 32+ (6m) = 32 m.

Total water capacity needed per day =50×4=200m3/ day .

Eh =0.002725×V × h T

=0.002725×200×32= 20.71 kwh / day

E p in   = 20.71 / .55 =37.65 k w h /day .

E ASM in = 37.65 / 0.82 = 45.9  K w h / day   .

E S.G in   = 45.9/0.75 = 61.2 kwh

E DIESEL in =61.2/0.30 = 204 kwh

Number of liters diesel needed daily = 204/10.5 =19.43 $

Diesel cost = 6* 19.43 NIS =116.58 NIS/day

COST OF EQUIPMENT :

Diesel and engine and S.G = 3125 $

Motor  pump set = 2000 $

Piping  and accessories = 500 $

Capital cost = 5625 $

| Capital cost | daily liter diesel needed of # | wells |
| --- | --- | --- |
| 4525 $ | 6 | رائد عويص Well depth=70m . 63 m3/ day |
| 4225 $ | 1.76 | جميل مساد Well depth=45m . 15 m3/ day |
| 4745 $ | 6.87 | خليل غانم Well depth=60m . 48 m3/ day |
| 4525 $ | 5.7 | احمد عامودي Well depth=60m . 36 m3/ day |
| 4125 $ | .78 | أنس مساد Well depth=40m . 7.5 m3/ day |
| 4525 $ | 6.06 | محمود العامودي Well depth=70m . 36 m3/ day |
| 5625 $ | 19.43 | كامل عمر ابراهيم عباس Well depth=50m . 200 m3/ day |

Chapter 5

The calculation of average value of yearly pumping water

(m3 / day)

رائد عويص

January

E pv out = 2.85 ×2.85 =8.12 kwh

15.42 kwh / day    →36 m3 / day

8.12 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 18.9 m3 / day.

February

Epv out = 2.85 ×3.2 =9.12 kwh

15.42 kwh / day    →36 m3 / day

9.12 kwh / day        →     ?

Average value of daily pumping water during February =21.29 m3 / day.

March

Epv out = 2.85 ×5.2 =14.82 kwh

15.42 kwh / day    →36 m3 / day

14.82 kwh / day        →     ?

Average value of daily pumping water during March   =34.59 m3 / day.

April

Epv out = 2.85 ×6.1 =17.38 kwh

15.42 kwh / day    →36 m3 / day

17.38 kwh / day        →     ?

Average value of daily pumping water during   April  =40.57 m3 / day.

May

Epv out = 2.85 ×7.6 =21.66 kwh

15.42 kwh / day    →36 m3 / day

21.66 kwh / day        →     ?

Average value of daily pumping water during  May    =50.56 m3 / day.

June

Epv out = 2.85 ×8.2 =23.37 kwh

15.42 kwh / day    →36 m3 / day

23.37 kwh / day        →     ?

Average value of daily pumping water during   june  =54.56 m3 / day.

July

Epv out = 2.85 ×8.1 =23.08  kwh

15.42 kwh / day    →36 m3 / day

23.08 kwh / day        →     ?

Average value of daily pumping water during   July    =53.88 m3 / day.

August

Epv out = 2.85 ×8 =22.8  kwh

15.42 kwh / day    →36 m3 / day

22.8  kwh / day        →     ?

Average value of daily pumping water during   August  =53.23 m3 / day.

September

Epv out = 2.85 ×6.2 =17.67 kwh

15.42 kwh / day    →36 m3 / day

17.67 kwh / day        →     ?

Average value of daily pumping water during   September=41.25 m3 / day.

October

Epv out = 2.85 ×4.7 =13.39 kwh

15.42 kwh / day    →36 m3 / day

13.39 kwh / day        →     ?

Average value of daily pumping water during   October   =31.26 m3 / day.

November

Epv out = 2.85 ×3.65 =10.4 kwh

15.42 kwh / day    →36 m3 / day

10.4 kwh / day        →     ?

Average value of daily pumping water during   November  =24.28 m3 / day.

December

Epv out = 2.85 ×2.9=8.26 kwh

15.42 kwh / day    →36 m3 / day

8.26  kwh / day        →     ?

Average value of daily pumping water during   December    =19.28 m3 / day.

Q year ==(19.28+24.28+31.26 +41.25+34.59+40.57+53.23+53.88

+54.56+50.56+14.82+21.29+18.9)×30                        =13757.1 m3 / year.

| m3 / day | Epv out | month |
| --- | --- | --- |
| 18.9 | 8.12 | January |
| 21.29 | 9.12 | February |
| 34.59 | 14.82 | march |
| 40.57 | 17.38 | April |
| 50.56 | 21.66 | May |
| 54.56 | 23.87 | June |
| 53.88 | 23.08 | July |
| 53.23 | 22.8 | August |
| 41.25 | 17.67 | September |
| 31.26 | 13.39 | October |
| 24.28 | 10.4 | November |
| 19.28 | 8.26 | December |

جميل مساد

January

E pv out = 2.85 ×.829 =2.36 kwh / day

4.48 kwh / day    →15 m3 / day

2.36 kwh / day        →     ?

Average value of daily pumping water during January =7.9 m3 / day.

February

Epv out = .829 ×3.2 =2.65 kwh / day

4.48 kwh / day    →15 m3 / day

2.65 kwh / day        →     ?

Average value of daily pumping water during February =8.87 m3 / day.

March

Epv out = .829 ×5.2 =4.31 kwh/ day

4.48 kwh / day    →15 m3 / day

4.31 kwh / day        →     ?

Average value of daily pumping water during March   =13.83 m3 / day.

April

Epv out = .829 ×6.1 =5.05 kwh / day

4.48 kwh / day    →15 m3 / day

17.38 kwh / day        →     ?

Average value of daily pumping water during   April  =16.9 m3 / day

May

Epv out = .829 ×7.6 =6.3 kwh

4.48 kwh / day    →15 m3 / day

6.3 kwh / day        →     ?

Average value of daily pumping water during  May    =21.09 m3 / day.

June

Epv out = .829 ×8.2 =6.79 kwh

4.48 kwh / day    →15 m3 / day

6.79 kwh / day        →     ?

Average value of daily pumping water during   June  =22.73 m3 / day.

July

Epv out = .829 ×8.1 =6.7  kwh

4.48 kwh / day    →15 m3 / day

6.7 kwh / day        →     ?

Average value of daily pumping water during   July    =22.43 m3 / day.

August

Epv out = .829 ×8 =6.63  kwh

4.48 kwh / day    →15 m3 / day

6.63  kwh / day        →     ?

Average value of daily pumping water during   August  =22.2 m3 / day.

September

Epv out = .829 ×6.2 =5.14 kwh

4.48 kwh / day    →15 m3 / day

5.14 kwh / day        →     ?

Average value of daily pumping water during   September=17.21 m3 / day.

October

Epv out = .829 ×4.7 =3.89 kwh

4.48 kwh / day    →15 m3 / day

3.89 kwh / day        →     ?

Average value of daily pumping water during   October   =13.04 m3 / day.

November

Epv out = .829 ×3.65 =3.02 kwh

4.48 kwh / day    →15 m3 / day

3.02 kwh / day        →     ?

Average value of daily pumping water during   November  = 10.13 m3 / day.

December

Epv out = .829 ×2.9=2.4 kwh .

4.48 kwh / day    →15 m3 / day

2.4  kwh / day        →     ?

Average value of daily pumping water during   December    =8.04 m3 / day.

Q year ==(8.04+10.13+16.9+13.83+8.87+7.9+21.09+13.04+17.21

+22.2+22.43+22.73)×30=9856.11 m3 / year.

| m3 / day | Epv out | month |
| --- | --- | --- |
| 7.9 | 2.36 | January |
| 13.83 | 8.87 | February |
| 13.83 | 4.31 | march |
| 16.9 | 5.05 | April |
| 21.09 | 6.3 | May |
| 22.73 | 6.79 | June |
| 22.43 | 6.7 | July |
| 22.2 | 6.63 | August |
| 17.21 | 5.14 | September |
| 13.04 | 3.89 | October |
| 10.13 | 3.02 | November |
| 8.04 | 2.4 | December |

**********************************************************

خليل غانم

January

E pv out = 2.85 ×3.23 =9.2 kwh / day

17.45 kwh / day    →48 m3 / day

9.2 kwh / day        →     ?

Average value of daily pumping water during January =25.3 m3 / day.

February

Epv out = 3.23 ×3.2 =10.33 kwh / day

17.45 kwh / day    →48 m3 / day

10.33 kwh / day        →     ?

Average value of daily pumping water during February =28.4 m3 / day.

March

Epv out = 3.23 ×5.2 =16.79 kwh/ day

17.45 kwh / day    →48 m3 / day

16.79 kwh / day        →     ?

Average value of daily pumping water during March   =46.18 m3 / day.

April

Epv out = 3.23 ×6.1 =19.7 kwh / day

17.45 kwh / day    →48 m3 / day

19.7 kwh / day        →     ?

Average value of daily pumping water during   April  =54.19 m3 / day.

May

Epv out = 3.23 ×7.6 =24.55 kwh

17.45 kwh / day    →48 m3 / day

24.55 kwh / day        →     ?

Average value of daily pumping water during  May    =67.53 m3 / day.

June

Epv out = 3.23 ×8.2 =26.48 kwh

17.45 kwh / day    →48 m3 / day

26.48 kwh / day        →     ?

Average value of daily pumping water during   June  =72.83 m3 / day.

July

Epv out = 3.23 ×8.1 =26.16  kwh

17.45 kwh / day    →48 m3 / day

26.16 kwh / day        →     ?

Average value of daily pumping water during   July    =71.96 m3 / day.

August

Epv out = 3.23 ×8 =25.84  kwh

17.45 kwh / day    →48 m3 / day

25.84  kwh / day        →     ?

Average value of daily pumping water during   August  =71.07 m3 / day.

September

Epv out = 3.23 ×6.2 =20.03 kwh

17.45 kwh / day    →48 m3 / day

20.03 kwh / day        →     ?

Average value of daily pumping water during   September=55.09 m3 / day.

October

Epv out = 3.23 ×4.7 =15.18 kwh

17.45 kwh / day    →48 m3 / day

15.18 kwh / day        →     ?

Average value of daily pumping water during   October   =41.75 m3 / day.

November

Epv out = 3.23 ×3.65 =11.79 kwh

17.45 kwh / day    →48 m3 / day

11.79 kwh / day        →     ?

Average value of daily pumping water during   November  = 32.43 m3 / day.

December

Epv out = 3.23 ×2.9=9.37 kwh .

17.45 kwh / day    →48 m3 / day

9.37 kwh / day        →     ?

Average value of daily pumping water during   December    =25.77 m3 / day.

Q year ==(25.77+54.19+46.18+28.4+25.3+32.43+67.53+72.83+

+71.96+71.07+55.04+41.75)×30=15998.1 m3 / year.

| m3 / day | Epv out | Month |
| --- | --- | --- |
| 25.3 | 9.2 | January |
| 28.4 | 10.33 | February |
| 46.18 | 16.79 | march |
| 54.19 | 19.7 | April |
| 67.53 | 24.55 | May |
| 72.83 | 26.48 | June |
| 71.96 | 26.16 | July |
| 11.84 | 25.84 | August |
| 55.09 | 20.03 | September |
| 41.75 | 15.18 | October |
| 32.43 | 11.79 | November |
| 25.77 | 9.37 | December |

احمد عامودي

January

E pv out = 2.85 ×2.68 =7.64 kwh / day

14.49 kwh / day    →36 m3 / day

7.64 kwh / day        →     ?

Average value of daily pumping water during January =18.98 m3 / day.

February

Epv out = 2.68 ×3.2 =8.576 kwh / day

14.49 kwh / day    →36 m3 / day

8.576 kwh / day        →     ?

Average value of daily pumping water during February =21.3 m3 / day.

March

Epv out = 2.68 ×5.2 =13.94 kwh/ day

14.49 kwh / day    →36 m3 / day

13.94 kwh / day        →     ?

Average value of daily pumping water during March   =34.63 m3 / day.

April

Epv out = 2.68 ×6.1 =16.35 kwh / day

14.49 kwh / day    →36 m3 / day

16.35 kwh / day        →     ?

Average value of daily pumping water during   April  =40.62 m3 / day.

May

Epv out = 2.68 ×7.6 =20.37 kwh

14.49 kwh / day    →36 m3 / day

20.37 kwh / day        →     ?

Average value of daily pumping water during  May    =50.61 m3 / day.

June

Epv out = 2.68 ×8.2 =21.97 kwh

14.49 kwh / day    →36 m3 / day

21.97 kwh / day        →     ?

Average value of daily pumping water during   June  =54.58 m3 / day.

July

Epv out = 2.68 ×8.1 =21.7   kwh

14.49 kwh / day    →36 m3 / day

21.7 kwh / day        →     ?

Average value of daily pumping water during   July    =53.9 m3 / day.

August

Epv out = 2.68 ×8 =21.44  kwh

14.49 kwh / day    →36 m3 / day

21.44  kwh / day        →     ?

Average value of daily pumping water during   August  =53.27 m3 / day.

September

Epv out = 2.68 ×6.2 =16.6 kwh

14.49 kwh / day    →36 m3 / day

16.6 kwh / day        →     ?

Average value of daily pumping water during   September=41.24 m3 / day.

October

Epv out = 2.68 ×4.7 =12.59 kwh

14.49 kwh / day    →36 m3 / day

12.59 kwh / day        →     ?

Average value of daily pumping water during   October   =31.28 m3 / day.

November

Epv out = 2.68 ×3.65 =9.78 kwh

14.49 kwh / day    →36 m3 / day

9.78 kwh / day        →     ?

Average value of daily pumping water during   November  = 24.29 m3 / day.

December

Epv out = 2.68 ×2.9=7.77 kwh .

14.49 kwh / day    →36 m3 / day

7.77 kwh / day        →     ?

Average value of daily pumping water during   December    =19.3 m3 / day.

Q year ==(19.3+24.29+31.28+18.98+21.3+34.63+40.62+50.61+

+54.58+53.9+53.27+41.24)×30=13320 m3 / year.

| m3 / day | Epv out | month |
| --- | --- | --- |
| 18.98 | 7.64 | January |
| 21.3 | 8.576 | February |
| 34.63 | 13.94 | march |
| 40.62 | 16.35 | April |
| 50.61 | 20.37 | May |
| 54.58 | 21.97 | June |
| 53.9 | 21.7 | July |
| 53.27 | 21.44 | August |
| 41.24 | 16.6 | September |
| 31.28 | 12.59 | October |
| 24.29 | 9.78 | November |
| 19.3 | 7.77 | December |

أنس مساد  .

January

E pv out = .37 ×2.85 =1.05 kwh / day

2 kwh / day    →7.5 m3 / day

1.05 kwh / day        →     ?

Average value of daily pumping water during January =3.9  m3 / day.

February

Epv out = .37 ×3.2 =1.184 kwh / day

2 kwh / day                 →7.5 m3 / day

1.184 kwh / day        →     ?

Average value of daily pumping water during February =4.44 m3 / day.

March

Epv out = .37 ×5.2 =1.92 kwh/ day

2 kwh / day    →7.5 m3 / day

1.92 kwh / day        →     ?

Average value of daily pumping water during March   =7.2 m3 / day.

April

Epv out = .37 ×6.1 =2.26 kwh / day

2   kwh / day    →7.5 m3 / day

2.26 kwh / day        →     ?

Average value of daily pumping water during   April  =8.48 m3 / day.

May

Epv out = .37×7.6 =2.81 kwh

2 kwh / day    →7.5 m3 / day

2.81 kwh / day        →     ?

Average value of daily pumping water during  May    =10.54 m3 / day.

June

Epv out = .37 ×8.2 =3.03 kwh

2 kwh / day    →7.5 m3 / day

3.03 kwh / day        →     ?

Average value of daily pumping water during   June  =11.36 m3 / day.

July

Epv out = .37 ×8.1 =3   kwh

2 kwh / day    →7.5 m3 / day

3kwh / day        →     ?

Average value of daily pumping water during   July    =11.25 m3 / day.

August

Epv out =.37 ×8 =2.96   kwh

2 kwh / day    →7.5 m3 / day

2.96   kwh / day        →     ?

Average value of daily pumping water during   August  =11.1 m3 / day.

September

Epv out = .37 ×6.2 =2.3 kwh

2 kwh / day    →7.5 m3 / day

2.3kwh / day        →     ?

Average value of daily pumping water during   September=8.63 m3 / day.

October

Epv out = .37 ×4.7 =1.74 kwh

2 kwh / day    →7.5 m3 / day

1.74 kwh / day        →     ?

Average value of daily pumping water during   October   =6.52 m3 / day.

November

Epv out = .37 ×3.65 =1.35 kwh

2 kwh / day    →7.5 m3 / day

1.35kwh / day        →     ?

Average value of daily pumping water during   November  = 5.06 m3 / day.

December

Epv out = .37 ×2.9=1.07 kwh .

2 kwh / day    →7.5 m3 / day

1.07 kwh / day        →     ?

Average value of daily pumping water during   December    =4.01 m3 / day.

Q year ==(4.01+5.06+6.52+3.9+4.44+7.2+8.48+10.54+

+11.36+11.25+11.1+8.63)×30=2774.7 m3 / year.

| m3 / day | Epv out | month |
| --- | --- | --- |
| 3.9 | 1.05 | January |
| 4.44 | 1.184 | February |
| 7.2 | 1.92 | march |
| 8.84 | 2.26 | April |
| 10.54 | 2.81 | May |
| 11.36 | 3.03 | June |
| 11.25 | 3 | July |
| 11.1 | 2.96 | August |
| 8.63 | 2.3 | September |
| 6.52 | 1.74 | October |
| 5.06 | 1.35 | November |
| 4.01 | 1.07 | December |

محمود العامودي

January

E pv out = 2.86 ×2.85 =8.15 kwh / day

15.42 kwh / day    →36 m3 / day

8.15 kwh / day        →     ?

Average value of daily pumping water during January =19.03  m3 / day.

February

Epv out = 2.86 ×3.2 =9.15 kwh / day

15.42 kwh / day    →36 m3 / day

9.15 kwh / day        →     ?

Average value of daily pumping water during February =21.36 m3 / day.

March

Epv out = 2.86 ×5.2 =12.87 kwh/ day

15.42 kwh / day    →36 m3 / day

1.92 kwh / day        →     ?

Average value of daily pumping water during March   =34.72 m3 / day.

April

Epv out = 2.86 ×6.1 =17.45 kwh / day

15.42 kwh / day    →36 m3 / day

17.45 kwh / day        →     ?

Average value of daily pumping water during   April  =40.74 m3 / day.

May

Epv out = 2.86×7.6 =21.74 kwh

15.42 kwh / day    →36 m3 / day

21.74 kwh / day        →     ?

Average value of daily pumping water during  May    =50.75 m3 / day.

June

Epv out = 2.86 × 8.2 =23.45 kwh

15.42 kwh / day    →36 m3 / day

23.45 kwh / day        →     ?

Average value of daily pumping water during   June  =54.75 m3 / day.

July

Epv out = 2.86 ×8.1 =23.2   kwh

15.42 kwh / day    →36 m3 / day

23.2kwh / day        →     ?

Average value of daily pumping water during   July    =54.08 m3 / day.

August

Epv out =2.86 ×8 =22.88   kwh

15.42 kwh / day    →36 m3 / day

22.88  kwh / day        →     ?

Average value of daily pumping water during   August  =53.42 m3 / day.

September

Epv out = 2.68  ×6.2 =17.73 kwh

15.42 kwh / day    →36 m3 / day

17.73 kwh / day        →     ?

Average value of daily pumping water during   September=41.39 m3 / day.

October

Epv out = 2.86 ×4.7 =13.44 kwh

15.42kwh / day    →36 m3 / day

13.44 kwh / day        →     ?

Average value of daily pumping water during   October   =31.38 m3 / day.

November

Epv out = 2.86 ×3.65 =10.44 kwh

15.42 kwh / day    →36 m3 / day

10.44 kwh / day        →     ?

Average value of daily pumping water during   November  = 24.37 m3 / day.

December

Epv out = 2.86 ×2.9=8.29 kwh .

15.42kwh / day    →36 m3 / day

8.29  kwh / day        →     ?

Average value of daily pumping water during   December    =19.35 m3 / day.

Q year ==(19.35+24.37+31.38+19.03+21.36+34.72+41.39+53.42+

+54.08+54.75+50.75+40.74)×30=13360.2 m3 / year.

| m3 / day | Epv out | month |
| --- | --- | --- |
| 19.03 | 8.15 | January |
| 21.36 | 9.15 | February |
| 34.72 | 14.87 | march |
| 40.74 | 17.45 | April |
| 50.75 | 21.74 | May |
| 54.75 | 23.45 | June |
| 54.08 | 23.2 | July |
| 53.42 | 22.88 | August |
| 41.39 | 17.73 | September |
| 31.38 | 13.44 | October |
| 24.37 | 10.44 | November |
| 19.35 | 8.29 | December |

كامل عمر ابراهيم عباس

January

E pv out = 2.85 ×9.14 =26.05 kwh

49.37 kwh / day    →200 m3 / day

26.05 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 105.5 m3 / day.

February

Epv out = 9.14 ×3.2 =29.25 kwh

49.37 kwh / day    →200 m3 / day

29.25 kwh / day        →     ?

Average value of daily pumping water during February =118.5 m3 / day.

March

Epv out = 9.14 ×5.2 =47.53 kwh

49.37 kwh / day    →200 m3 / day

47.53 kwh / day        →     ?

Average value of daily pumping water during March   =192.54 m3 / day.

April

Epv out = 9.14 ×6.1 =55.75 kwh

49.37 kwh / day    →200 m3 / day

55.75 kwh / day        →     ?

Average value of daily pumping water during   April  =225.86 m3 / day.

May

Epv out = 9.14 ×7.6 =69.46 kwh

49.37 kwh / day    →200 m3 / day

69.46 kwh / day        →     ?

Average value of daily pumping water during  May    =281.4 m3 / day.

June

Epv out = 9.14 ×8.2 =74.95 kwh

49.37 kwh / day    →200 m3 / day

74.95 kwh / day        →     ?

Average value of daily pumping water during   june  =303.62 m3 / day.

July

Epv out = 9.14 ×8.1 =74.03  kwh

49.37 kwh / day    →200 m3 / day

74.03 kwh / day        →     ?

Average value of daily pumping water during   July    =299.91 m3 / day.

August

Epv out = 9.14 ×8 =73.12  kwh

49.37 kwh / day    →200 m3 / day

73.12  kwh / day        →     ?

Average value of daily pumping water during   August  =296.2 m3 / day.

September

Epv out = 9.14×6.2 =56.7 kwh

49.37 kwh / day    →200 m3 / day

56.7 kwh / day        →     ?

Average value of daily pumping water during   September=229.7 m3 / day.

October

Epv out = 9.14 ×4.7 =42.96 kwh

49.37 kwh / day    →200 m3 / day

42.96 kwh / day        →     ?

Average value of daily pumping water during   October   =174.02 m3 / day.

November

Epv out = 9.14×3.65 =33.36kwh

49.37 kwh / day    →200 m3 / day

33.36 kwh / day        →     ?

Average value of daily pumping water during   November  =135.15 m3 / day.

December

Epv out = 9.14 ×2.9=26.51 kwh

49.37 kwh / day    →200m3 / day

26.51  kwh / day        →     ?

Average value of daily pumping water during   December    =107.4 m3 / day.

Q year ==(105.5+118.5+192.54+225.86+281.4+303.62+299.91+296.2+

229.7+174.02+135.15+107.4)×30

=74094 m3 / year

| month | Epv out | m3 / day |
| --- | --- | --- |
| January | 26.05 | 105.5 |
| February | 26.25 | 118.5 |
| march | 47.53 | 192.54 |
| April | 55.75 | 225.86 |
| May | 69.46 | 281.4 |
| June | 74.95 | 303.62 |
| July | 74.03 | 299.91 |
| August | 73.12 | 296.2 |
| September | 56.7 | 229.7 |
| October | 42.96 | 174.02 |
| November | 33.36 | 135.15 |
| December | 26.15 | 107.4 |

| wells | Q year (m3 / year) |
| --- | --- |
| رائد عويس | 13757.1 |
| جميل مساد | 9856.11 |
| خليل غانم | 15998.1 |
| احمد العامودي | 13320 |
| أنس مساد | 2774.7 |
| محمود العامودي | 13360.2 |
| كامل عمر ابراهيم عباس | 74094 |

Chapter 6

Economical evaluation of energy supply systems

Introduction:

Engineers seek solutions to problems, and the economic viability of each

potential solution is normally considered along with the technical

aspects.

For each design, there are usually many possible alternatives. One option

that must be considered in each analysis is often the choice which

achieves technical aspects and the opportunity cost of making one choice

over another must also be considered.

In this chapter, we will study each possible solution in economic point

view to select optimum configuration.

6-1 The economic evaluation of  Pv power system for wells:

رائد عويص

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=2361.55 KWh/year.

- The  total fixed cost of this system = 10325 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*10325 = 1032.5$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 10325 = 258.125 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 1032.5 + 258.125 = 1290.625 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)=1290.625/2361.55 = 0.546 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 1290.625 $.

Q=13757.1 m3/ year.

The cost of 1 m3  =1290.625/13757.1= .0938  m3/ year.

For Jameel well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=686.2 KWh/year.

- The  total fixed cost of this system = 4572.5 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4572.5 = 457.25$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 4572.5 = 114.31 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 457.25 + 114.31 = 571.5625 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)=571.5625/686.2 = 0.83 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 571.5625 $.

Q=9856.11 m3/ year.

The cost of 1 m3  =571.5625 /9856.11 = .058  m3/ year.

For khaleeel well;

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=2671.8 KWh/year.

- The  total fixed cost of this system = 11695 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*11695= 1169.5$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 11695 = 292.375 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 1169.5 + 292.375 = 1461.875 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 1461.875 /2671.8  = 0.547 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost =1461.875  $.

Q=15998.1m3/ year.

The cost of 1 m3  =1461.875 /15998.1 = .0914  m3/ year.

**********************************************************

For Ahmad well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=2219.2 KWh/year.

- The  total fixed cost of this system = 9900 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*9900= 990$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 9900 = 247.5 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 990 + 247.5 = 1237.5 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 1237.5   /2219.2  = 0.557 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost =1237.5  $.

Q=13320 m3/ year.

The cost of 1 m3  =1237.5 /13320= .0914  m3/ year.

******************************************************************

For Anas well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=306.6 KWh/year.

- The  total fixed cost of this system = 3225 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*3225= 322.5$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 3225 = 80.625 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 322.5 + 80.625 = 403.125 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 403.125  /306.6  = 1.3 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost =403.125  $.

Q=2774.7 m3/ year.

The cost of 1 m3  =403.125 /2774.7= .145  m3/ year.

******************************************************************

For Mahmood well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the pv syste=2361.55 KWh/year.

- The  total fixed cost of this system = 10325 $

- Depreciation factor = 10 % .

- Maintenance cost = 2.5 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*103 = 1035$ .

Annual running cost = maintenance cost

Annual running cost = 0.025 * 10350 = 258.75 $.

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 1035 + 258.75 = 1293.75 $.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)=1293.75/2361.55 = 0.547 $/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 1293.75 $.

Q=13360.2 m3/ year.

The cost of 1 m3  =1293.75/13360.2= .097  m3/ year

6-2  The economic evaluation of diesel  power system for wells:

For Raad well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the  diesel syste=2361.55 KWh/year.

- The  total fixed cost of this system = 4525 $

- Diesel cost = 9.09$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4525 = 452.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 4452.85$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 4905.35$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 2$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 4905.35$.

Q=13140 m3/ year.

The cost of 1 m3  =4905.35/13140= .373  m3/ year.

**********************************************************

For Jameel well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the diesel system=686.2KWh/year.

- The  total fixed cost of this system = 4225 $

- Diesel cost = 2.64$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4225 = 422.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 1597.35$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 2019.85$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 2.9$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 2019.85$.

Q=5475 m3/ year.

The cost of 1 m3  = .369  m3/ year.

**********************************************************

For Khaleel well ;

Evaluation of the cost of 1 KWh :

- Total energy out from thediesel  system=2635.3KWh/year.

- The  total fixed cost of this system = 4745 $

- Diesel cost = 10.3$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4745 = 474.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 4929.325$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 5403.825$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 2$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 5403.825$.

Q=17520 m3/ year.

The cost of 1 m3  = .308  m3/ year.

**********************************************************

For Ahmad well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the diesel system=2219.2 KWh/year.

- The  total fixed cost of this system = 4525 $

- Diesel cost = 8.55$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4525 = 452.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 4018.5$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 4471$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 2$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 4471$.

Q=13140 m3/ year.

The cost of 1 m3  =.34m3/ year.

**********************************************************

For Anas well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the diesel system=306.6KWh/year.

- The  total fixed cost of this system = 4125 $

- Diesel cost = 1.17$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4125 = 412.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 1045.8$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 1458.3$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 3.5$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 1458.3$.

Q=2737.5 m3/ year.

The cost of 1 m3  = .533  m3/ year.

********************************************************

For Mahmoud well ;

Evaluation of the cost of 1 KWh :

- Total energy out from the  diesel syste=2361.55 KWh/year.

- The  total fixed cost of this system = 4525 $

- Diesel cost = 9.09$/day.

- Depreciation factor = 10 % .

- Maintenance cost = 15 % fixed cost .

Annual fixed cost = depreciation factor * total fixed cost                               Annual fixed cost = 0.1*4525 = 452.5$ .

Annual running cost = maintenance cost +diesel cost + oil cost

Annual running cost = 4452.85$

Total annual cost =total Annual fixed cost + total Annual running cost.

Total annual cost = 4905.35$.

The cost of unit generated (1 KWh) = total annual cost / total energy output.

The cost of unit generated (1 KWh)= 2$/kwh.

Evaluation of the cost of 1 m3 :

Total annual cost = 4905.35$.

Q=13140 m3/ year.

The cost of 1 m3  =4905.35/13140= .373  m3/ year.

The table below shows the associated cost of 1kwh generated from each configuration:

| The cost of 1 Kwh in $ |  |  |
| --- | --- | --- |
| System type Wells | PV system | Diesel system |
| Raad well | .546 | 2 |
| Jameel well | .83 | 2.9 |
| Khaleel well | .547 | 2 |
| Ahmad well | .557 | 2 |
| Anas well | 1.3 | 3.5 |
| Mahmoud well | .547 | 2 |

| The cost of 1 m3 in $ |  |  |
| --- | --- | --- |
| System type Wells | PV system | Diesel system |
| Raad well | .0938 | .373 |
| Jameel well | .o58 | .369 |
| Khaleel well | .0914 | .308 |
| Ahmad well | .093 | .34 |
| Anas well | .145 | .533 |
| Mahmoud well | .097 | .373 |

Chapter 7

Net present value ( NPV )

Net present value ( NPV )

The NPV of an investment project at time t=0 is the sum of the present values of all cash inflows and outflows linked to the investment :

NPV = -I0 + (Rt –It)q-t  + LTq-T

q-t = (1+)-t

where I0 is the investment cost at the beginning (t=0) ,T is the life time of project in years, Rt is the return in time period  t , It  is the investment in time period t , q-t  is discounting  factor , i is the discount rate and LT is the salvage value .

A project is profitable when NPV0 and the greater the NPV the more profitable.

Negative NPV indicates that minimum interest  rate will not be met.

Net  Present Value

For Raad well

NPV= 520(P/F,8%,20) +4400 (P/A,8%,20) -250(P/A,8%,20) -10325 =30473.3  $

**********************************************************

For  jameel well

NPV= 230(P/F,8%,20) +1500 (P/A,8%,20) -110(P/A,8%,20) -4572.5=9123.85  $

For khaleel well

NPV= 600(P/F,8%,20) +4900 (P/A,8%,20) -290(P/A,8%,20) -11695=33694.6  $

**********************************************************

For Ahmad well

NPV= 500(P/F,8%,20) +4000 (P/A,8%,20) -250(P/A,8%,20) -9900=27024.75  $

For Anas well

NPV = 160(P/F,8%,20) +1000 (P/A,8%,20) -80(P/A,8%,20) -3225=5841.88  $

for  Mahmood  well

NPV = 510(P/F,8%,20) +4400 (P/A,8%,20) -260(P/A,8%,20) -10350=30405.9$

Chapter 8

Life cycle cost

Life cycle cost

For Raad  well

PV system

PW = 520(P/F,8%,20) -260(P/A,8%,20) -10325= -12766.14 $

Diesel system

PW = 230(P/F,8%,20) - 4400(P/A,8%,20)  -4522-4292(P/F,8%,10)= -49659.9 $

For Jameel well

PV system

PW = 230(P/F,8%,20) -110(P/A, 8%,20) -4572= -5602,645 $

Diesel  system

PW = 220(P/F,8%,20) - 1500(P/A,8%,20)  -4225-4005(P/F,8%,10)= -20759.9 $

For Khaleel well

PV system

PW = 600(P/F,8%,20) -290(P/A, 8%,20) -11695= -14413 $

Diesel system

PW = 240(P/F,8%,20) - 4900(P/A,8%,20)  -4745-4505(P/F,8%,10)= -54888.4 $

For Ahmad well

PV system

PW = 500(P/F,8%,20) -250(P/A, 8%,20) -9900= -12247 $

Diesel system

PW = 230(P/F,8%,20) - 4400(P/A,8%,20)  -4522-4292(P/F,8%,10)= -49659.9 $

Evaluation results and conclusions

Based on above results the following conclusion can be made :

- The annuity and the production cost of energy uint (KWh) of PV-system are less than the diesel system.

- The net present value ( NPV)of the PV-system is much higher than the NPV of diesel system.

- The life cycle cost of the PV-system is less than the diesel system.

Therefore , utitizing of PV-system is more economic feasible for pumping water .in additional the PV-system do not pollute the environment as the case of using diesel generator.

Chapter 9

Breakeven point

9 -1 The  calculation of $/ m3 for pv system

1- 60 m3/day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =   5m3/ hour   for 12 hour / day .

Total pumping head (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =5*12 =60

Eh =0.002725×V × hT

=0.002725×60×56= 9.156kwh / day

E p in  =(9.156 kwh /day)/.55 =16.65 kwh/day.

E ASM in  = (16.65 Kwh / day ) /.82= 20.3 kwh /day.

Einv in=21.82

1 kWp ----------- 5.4 kwh/day

?? ----------------- 21.82 kwh/day

21.82 kwh/day --------------60 m3/day

January

E pv out = 2.85 ×4.04 =11.514 kwh

21.82 kwh/day --------------60 m3/day

11.514 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 31.66m3 / day.

February

Epv out = 4.04 ×3.2 =12.93 kwh

21.82 kwh/day --------------60 m3/day

12.93 kwh / day        →     ?

Average value of daily pumping water during February =35.55 m3 / day.

March

Epv out = 4.04 ×5.2 =21.01 kwh

21.82 kwh/day --------------60 m3/day

21.01 kwh / day        →     ?

Average value of daily pumping water during March   =57.76 m3 / day.

April

Epv out = 4.04 ×6.1 =24.64 kwh

21.82 kwh/day --------------60 m3/day

24.64 kwh / day        →     ?

Average value of daily pumping water during   April  =67.77 m3 / day.

May

Epv out = 4.04 ×7.6 =30.704 kwh

21.82 kwh/day --------------60 m3/day

30.704 kwh / day        →     ?

Average value of daily pumping water during  May    =84.43 m3 / day.

June

Epv out = 4.04 ×8.2 =33.13 kwh

21.82 kwh/day --------------60 m3/day

33.13 kwh / day        →     ?

Average value of daily pumping water during   june  =91.09 m3 / day.

July

Epv out = 4.04 ×8.1 =32.72  kwh

21.82 kwh/day --------------60 m3/day

32.72 kwh / day        →     ?

Average value of daily pumping water during   July    =89.98 m3 / day.

August

Epv out = 4.04 ×8 =32.32  kwh

21.82 kwh/day --------------60 m3/day

32.32  kwh / day        →     ?

Average value of daily pumping water during   August  =88.87 m3 / day.

September

Epv out = 4.04 ×6.2 =25.05kwh

21.82 kwh/day --------------60 m3/day

25.05 kwh / day        →     ?

Average value of daily pumping water during   September=68.88 m3 / day.

October

Epv out = 4.04 ×4.7 =18.99 kwh

21.82 kwh/day --------------60 m3/day

18.99 kwh / day        →     ?

Average value of daily pumping water during   October   =52.21 m3 / day.

November

Epv out = 4.04 ×3.65 =14.75kwh

21.82 kwh/day --------------60 m3/day

14.75 kwh / day        →     ?

Average value of daily pumping water during   November  =40.55m3 / day.

December

Epv out = 4.04 ×2.9=11.72 kwh

21.82 kwh/day --------------60 m3/day

11.72  kwh / day        →     ?

Average value of daily pumping water during   December    =32.22 m3 / day.

Q year =*30

=22229.1 m3 / year.

Total energy  from pv system

Eh*365=3341.94 kwh/year

1 wp  --------------2.5$

4040wp  ------------?

10100$ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost= 10100+2200+1400+450 = 14150$

Annual fixed cost = .1 *capital cost         = .1* 14150 =1415$

Maintenance cost = .025* capital cost = .025* 14150= 353.75 $/year

Total annual cost= total fixed cost + total running cost

= 1415+353.75=1768.75 $/year

Cost of (1kwh)= total annual cost /total energy =1768.75/3341.94=.53 $/year

$/m3 = total annual cost/ total pumping rate = 1768.75/22229.1 =.0796 $/m3

2 - 80 m3/day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =   4m3/ hour   for 20 hour / day .

Total pumping head (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =80m3/day

Eh =0.002725×V × hT

=0.002725×80×56= 12.208kwh / day

E p in  =(12.208 kwh /day)/.55 =22.2 kwh/day.

E ASM in  = (22.2 Kwh / day ) /.82= 27.068 kwh /day.

Einv in=29.106

1 kWp ----------- 5.4 kwh/day

?? ----------------- 29.82kwh/day

21.82 kwh/day --------------60 m3/day

January

E pv out = 2.85 ×5.39 =15.36 kwh

21.82 kwh/day --------------60 m3/day

15.36 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 41.21m3 / day.

February

Epv out = 5.39 ×3.2 =17.248 kwh

21.82 kwh/day --------------60 m3/day

17.248 kwh / day        →     ?

Average value of daily pumping water during February =46.27m3 / day.

March

Epv out = 5.39 ×5.2 =28.03 kwh

21.82 kwh/day --------------60 m3/day

28.03 kwh / day        →     ?

Average value of daily pumping water during March   =75.19 m3 / day.

April

Epv out = 5.39 ×6.1 =32.88 kwh

21.82 kwh/day --------------60 m3/day

32.88 kwh / day        →     ?

Average value of daily pumping water during   April  =88.21 m3 / day.

May

Epv out = 5.39 ×7.6 =40.96 kwh

21.82 kwh/day --------------60 m3/day

40.96 kwh / day        →     ?

Average value of daily pumping water during  May    =109.89 m3 / day.

June

Epv out = 5.39 ×8.2 =44.198 kwh

21.82 kwh/day --------------60 m3/day

44.198 kwh / day        →     ?

Average value of daily pumping water during   june  =118.57 m3 / day.

July

Epv out = 5.39 ×8.1 =43.66  kwh

21.82 kwh/day --------------60 m3/day

43.66 kwh / day        →     ?

Average value of daily pumping water during   July    =117.13 m3 / day.

August

Epv out = 5.39 ×8 =43.12  kwh

21.82 kwh/day --------------60 m3/day

43.12  kwh / day        →     ?

Average value of daily pumping water during   August  =115.68 m3 / day.

September

Epv out = 5.39 ×6.2 =33.418kwh

21.82 kwh/day --------------60 m3/day

33.418 kwh / day        →     ?

Average value of daily pumping water during   September=89.65 m3 / day.

October

Epv out = 5.39 ×4.7 =25.33kwh

21.82 kwh/day --------------60 m3/day

25.33 kwh / day        →     ?

Average value of daily pumping water during   October   =67.96 m3 / day.

November

Epv out = 5.39 ×3.65 =19.67kwh

21.82 kwh/day --------------60 m3/day

19.67 kwh / day        →     ?

Average value of daily pumping water during   November  =52.78m3 / day.

December

Epv out =5.39 ×2.9=15.63 kwh

21.82 kwh/day --------------60 m3/day

15.63  kwh / day        →     ?

Average value of daily pumping water during   December    =41.93 m3 / day.

Q year =*30

=28934.1 m3 / year.

Total energy  from pv system

Eh*365=4455.92 kwh/year

1 wp  --------------2.5$

5390wp  ------------?

13475$ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost= 13475+2500+1600+500 = 18075$

Annual fixed cost = .1 *capital cost         = .1* 18075 =1807.5$

Maintenance cost = .025* capital cost = .025* 18075= 451.875 $/year

Total annual cost= total fixed cost + total running cost

= 1807.5+341.875=2149.375 $/year

Cost of (1kwh)= total annual cost /total energy =2149.375/4455.92=.48$/year

$/m3 = total annual cost/ total pumping rate = 2149.375/28934.1 =.0746 $/m3

3 - 120 m3/day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =   30m3/ hour   for 4hour / day .

Total pumping head (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =120m3/day

Eh =0.002725×V × hT

=0.002725×120×56= 18.312kwh / day

E p in  =(18.312 kwh /day)/.55 =33.29 kwh/day.

E ASM in  = (33.29 Kwh / day ) /.82= 40.603kwh /day.

Einv in=43.66

1 kWp ----------- 5.4 kwh/day

?? ----------------- 43.66 kwh/day

43.66 kwh/day --------------120 m3/day

January

E pv out = 2.85 ×8.085=23.04kwh

21.82 kwh/day --------------60 m3/day

23.04 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 63.32m3 / day.

February

Epv out = 8.085×3.2 =25.87 kwh

21.82 kwh/day --------------60 m3/day

28.87 kwh / day        →     ?

Average value of daily pumping water during February =71.1 m3 / day.

March

Epv out = 8.085×5.2 =42.04 kwh

21.82 kwh/day --------------60 m3/day

42.04 kwh / day        →     ?

Average value of daily pumping water during March   =115.54 m3 / day.

April

Epv out =8.085×6.1 =49.31 kwh

21.82 kwh/day --------------60 m3/day

49.31 kwh / day        →     ?

Average value of daily pumping water during   April  =135.54 m3 / day.

May

Epv out = 8.085×7.6 =61.4884 kwh

21.82 kwh/day --------------60 m3/day

61.4884 kwh / day        →     ?

Average value of daily pumping water during  May    =168.86 m3 / day.

June

Epv out = 8.085×8.2 =66.29 kwh

21.82 kwh/day --------------60 m3/day

66.29 kwh / day        →     ?

Average value of daily pumping water during   june  =182.2 m3 / day.

July

Epv out =8.085×8.1 =65.48  kwh

21.82 kwh/day --------------60 m3/day

65.48 kwh / day        →     ?

Average value of daily pumping water during   July    =179.97 m3 / day.

August

Epv out = 8.085×8 =64.67  kwh

21.82 kwh/day --------------60 m3/day

64.67  kwh / day        →     ?

Average value of daily pumping water during   August  =177.75 m3 / day.

September

Epv out = 8.085×6.2 =50.12kwh

21.82 kwh/day --------------60 m3/day

50.12 kwh / day        →     ?

Average value of daily pumping water during   September=137.76 m3 / day.

October

Epv out = 8.085×4.7 =38.0 kwh

21.82 kwh/day --------------60 m3/day

38.0 kwh / day        →     ?

Average value of daily pumping water during   October   =104.42m3 / day.

November

Epv out = 8.085×3.65 =29.51kwh

21.82 kwh/day --------------60 m3/day

29.51 kwh / day        →     ?

Average value of daily pumping water during   November  =81.1m3 / day.

December

Epv out = 8.085×2.9=23.44 kwh

21.82 kwh/day --------------60 m3/day

23.44  kwh / day        →     ?

Average value of daily pumping water during   December    =64.43 m3 / day.

Q year =*30

=44459.7 m3 / year.

Total energy  from pv system

Eh*365=6683.88 kwh/year

1 wp  --------------2.5$

18312wp  ------------?

45780$ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost= 45780+3000+2200+500 =51480$

Annual fixed cost = .1 *capital cost         = .1* 51480=5148$

Maintenance cost = .025* capital cost = .025* 51480= 1287$/year

Total annual cost= total fixed cost + total running cost

= 5148+1287=6435 $/year

Cost of (1kwh)= total annual cost /total energy =6435/6683.88=.96$/year

$/m3 = total annual cost/ total pumping rate = 6435/44459.7 =.145 $/m3

4 - 35 m3/day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2inch.

Compute of the well =     3  m3/ hour       ,12 hour / day .

Total pumping head  (ht) = 50 +(6m) = 56m.

Total water capacity needed per day =3 ×12=35 m3

Eh =0.002725×V × hT

=0.002725×35 ×56= 5.341 kwh / day

E p in  =5.341 /.55 =9.7 kwh /day .

E asm in =9.7 / .82 = 11.83 Kwh / day  .

E inv in =11.83 /.92 =12.86 kwh / day .

Psh =5.4 kwh /day.

1kwp       →5.4 kwh /day.

?       → 12.86  kwh / day.

PPV= 2.38 kwp .

Pv   →   1 wp  = 2.5 $

January

E pv out = 2.85 ×2.38 =6.78kwh

12.86 kwh / day    →35 m3 / day

6.78 kwh / day        →     ?

Average value of daily pumping water dnring January

→ 18.45  m3 / day.

February

Epv out = 3.2 ×2.38 =7.62  kwh

12.86 kwh / day    →35 m3 / day

7.62 kwh / day        →     ?

Average value of daily pumping water during February =20.7 m3 / day.

March

Epv out = 5.2 ×2.38 =12.376 kwh

12.86 kwh / day    →35 m3 / day

12.375 kwh / day        →     ?

Average value of daily pumping water during March   = 33.86 m3 / day.

April

Epv out = 6.1 ×2.38 =14.5 kwh

12.375 kwh / day    →35 m3 / day

14.5  kwh / day        →     ?

Average value of daily pumping water during   April  =39.5 m3 / day.

May

Epv out = 7.6 ×2.38 = 18 kwh

12.86 kwh / day    →35 m3 / day

18 kwh / day        →     ?

Average value of daily pumping water during  May    =48.98 m3 / day.

June

Epv out = 8.2 ×2.38 =19.51 kwh

12.86 kwh / day    →35 m3 / day

19.51 kwh / day        →     ?

Average value of daily pumping water during   june  =53 m3 / day.

July

Epv out =8.1 ×2.38 =19.27  kwh

12.86 kwh / day    →35 m3 / day

19.27 kwh / day        →     ?

Average value of daily pumping water during   July    =52.46 m3 / day.

August

Epv out = 8 ×2.38 =19.04  kwh

12.86 kwh / day    →35 m3 / day

19.04  kwh / day        →     ?

Average value of daily pumping water during   August  =51.82 m3 / day.

September

Epv out = 6.2 ×2.28 =14.75 kwh

12.86 kwh / day    →35 m3 / day

14.75 kwh / day        →     ?

Average value of daily pumping water during   September=40 m3 / day.

October

Epv out = 4.7 ×2.38 =11.86 kwh

12.86 kwh / day    →35 m3 / day

11.86 kwh / day        →     ?

Average value of daily pumping water during   October   =30.44 m3 / day.

November

Epv out =3.65  ×2.38 =8.687 kwh

12.86 kwh / day    →35 m3 / day

8.687 kwh / day        →     ?

Average value of daily pumping water during   November  =23.64 m3 / day.

December

Epv out = 2.9 ×2.38=6.9 kwh

12.86 kwh / day    →35 m3 / day

6.9  kwh / day        →     ?

Average value of daily pumping water during   December    =18.78 m3 / day.

Q year ==(18.78+23.64+18.45 +20.7+33.86+39.5+48.98+

+53+52.46+51.82+40+30.44)×30

=12948.9 m3 / year.

Total energy  from pv system

Eh*365=1949.465 kwh/year

1 wp  --------------2.5$

2380wp  ------------?

5950 $ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost=5950+1780+1000+400 =9130$

Annual fixed cost = .1 *capital cost         = .1*9130=9138$

Maintenance cost = .025* capital cost = .025* 9130= 228.25$/year

Total annual cost= total fixed cost + total running cost

= 913+228.25=1141.25 $/year

Cost of (1kwh)= total annual cost /total energy =1141.25/1949.465=.585$/year

$/m3 = total annual cost/ total pumping rate = 1141.25/12948.9 =.088 $/m3

5 - 20 m3/day

Well depth=60m.

Swl = 30m.

Dwl =50 m.

Pipe = 2inch.

Output of the well =  4m3/ hour   for  5 hour / day .

Total pumping head  (hT) = 50 +(6m) = 46m.

Total water capacity needed per day =4 ×5=20 m3

Eh =0.002725×V × hT

=0.002725×20×56= 3.052kwh / day

E p in  =3.052 /.55=5.55 kwh /day .

E ASM in =5.55 /.82  =6.77  Kwh / day  .

E inv in =6.77 /.92 =7.358 kwh / day .

Psh =5.4 kwh /day.

1kwp       →5.4 kwh /day.

?       → 7.358 kwh / day.

PPV= 1.36 kwp .

January

E pv out = 2.85 ×1.36 =3.876 kwh / day

7.358 kwh / day    →20 m3 / day

3.876 kwh / day        →     ?

Average value of daily pumping water during January =10.53 m3 / day.

February

Epv out = 3.2 ×1.36 =4.35 kwh / day

7.358 kwh / day    →20 m3 / day

4.35 kwh / day        →     ?

Average value of daily pumping water during February =11.82 m3 / day.

March

Epv out = 5.2 ×1.36 =7.07 kwh/ day

7.358 kwh / day    →20 m3 / day

7.07 kwh / day        →     ?

Average value of daily pumping water during March   =19.22 m3 / day.

April

Epv out = 6.1 ×1.36 =8.296 kwh / day

7.358 kwh / day    →20 m3 / day

8.296 kwh / day        →     ?

Average value of daily pumping water during   April  =22.55 m3 / day.

May

Epv out = 7.6 ×1.36 =10.336 kwh

7.358 kwh / day    →20 m3 / day

10.336 kwh / day        →     ?

Average value of daily pumping water during  May    =28 m3 / day.

June

Epv out = 8.2 ×1.36 =11.152 kwh

30.3 kwh / day    →20 m3 / day

11.152 kwh / day        →     ?

Average value of daily pumping water during   June  =30.3 m3 / day.

July

Epv out = 8.1 ×1.36 =29.89  kwh

7.358 kwh / day    →20 m3 / day

29.89 kwh / day        →     ?

Average value of daily pumping water during   July    =29.89 m3 / day.

August

Epv out = 8 ×1.36 =29.57  kwh

7.358 kwh / day    →20 m3 / day

29.57  kwh / day        →     ?

Average value of daily pumping water during   August  =29.57 m3 / day.

September

Epv out = 6.2 ×1.36 =8.43 kwh

7.358 kwh / day    →20 m3 / day

8.43 kwh / day        →     ?

Average value of daily pumping water during   September=22.91 m3 / day.

October

Epv out = 4.7 ×1.36 =6.39 kwh

7.358 kwh / day    →20 m3 / day

6.39 kwh / day        →     ?

Average value of daily pumping water during   October   =17.368 m3 / day.

November

Epv out = 3.65 ×1.36 =4.96 kwh

7.358 kwh / day    →20 m3 / day

4.96 kwh / day        →     ?

Average value of daily pumping water during   November  =13.48 m3 / day.

December

Epv out = 2.9 ×1.36=3.94 kwh .

7.358 kwh / day    →20 m3 / day

3.94  kwh / day        →     ?

Average value of daily pumping water during   December    =10.7 m3 / day.

Q year ==(22.55+28+30.3+29.89+29.57+22.91+17.368+13.48+10.7+                                      19.22 +11.82+10.53+)×30=9856.11 m3 / year.

Total energy  from pv system

Eh*365=1113.98 kwh/year

1 wp  --------------2.5$

1360wp  ------------?

3400$ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost= 3400+1670+600+350 =6020$

Annual fixed cost = .1 *capital cost         = .1*6020=602$

Maintenance cost = .025* capital cost = .025*6020= 150.5 $/year

Total annual cost= total fixed cost + total running cost

=150.5+602=752.5 $/year

Cost of (1kwh)= total annual cost /total energy =752.5/1113.98=.6755 $/year

$/m3 = total annual cost/ total pumping rate =752.5/7390.14 =.098 $/m3

6  - 48 m3 / day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2inch.

Output of the well =  4 m3/ hour   for  12 hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =4 ×12=48 m3

Eh =0.002725×V × hT

=0.002725×48×56= 7.32kwh / day

E p in  =13.3 kwh /day .

E ASM in  = 16.23  Kwh / day  .

E inv in = =17.45 kwh / day .

Psh =5.4 kwh /day.

1kwp       →5.4 kwh /day.

?       → 17.45 kwh / day.

PPV= 3.23 kwp .

January

E pv out = 2.85 ×3.23 =9.2 kwh / day

17.45 kwh / day    →48 m3 / day

9.2 kwh / day        →     ?

Average value of daily pumping water during January =25.3 m3 / day.

February

Epv out = 3.23 ×3.2 =10.33 kwh / day

17.45 kwh / day    →48 m3 / day

10.33 kwh / day        →     ?

Average value of daily pumping water during February =28.4 m3 / day.

March

Epv out = 3.23 ×5.2 =16.79 kwh/ day

17.45 kwh / day    →48 m3 / day

16.79 kwh / day        →     ?

Average value of daily pumping water during March   =46.18 m3 / day.

April

Epv out = 3.23 ×6.1 =19.7 kwh / day

17.45 kwh / day    →48 m3 / day

19.7 kwh / day        →     ?

Average value of daily pumping water during   April  =54.19 m3 / day.

May

Epv out = 3.23 ×7.6 =24.55 kwh

17.45 kwh / day    →48 m3 / day

24.55 kwh / day        →     ?

Average value of daily pumping water during  May    =67.53 m3 / day.

June

Epv out = 3.23 ×8.2 =26.48 kwh

17.45 kwh / day    →48 m3 / day

26.48 kwh / day        →     ?

Average value of daily pumping water during   June  =72.83 m3 / day.

July

Epv out = 3.23 ×8.1 =26.16  kwh

17.45 kwh / day    →48 m3 / day

26.16 kwh / day        →     ?

Average value of daily pumping water during   July    =71.96 m3 / day.

August

Epv out = 3.23 ×8 =25.84  kwh

17.45 kwh / day    →48 m3 / day

25.84  kwh / day        →     ?

Average value of daily pumping water during   August  =71.07 m3 / day.

September

Epv out = 3.23 ×6.2 =20.03 kwh

17.45 kwh / day    →48 m3 / day

20.03 kwh / day        →     ?

Average value of daily pumping water during   September=55.09 m3 / day.

October

Epv out = 3.23 ×4.7 =15.18 kwh

17.45 kwh / day    →48 m3 / day

15.18 kwh / day        →     ?

Average value of daily pumping water during   October   =41.75 m3 / day.

November

Epv out = 3.23 ×3.65 =11.79 kwh

17.45 kwh / day    →48 m3 / day

11.79 kwh / day        →     ?

Average value of daily pumping water during   November  = 32.43 m3 / day.

December

Epv out = 3.23 ×2.9=9.37 kwh .

17.45 kwh / day    →48 m3 / day

9.37 kwh / day        →     ?

Average value of daily pumping water during   December    =25.77 m3 / day.

Q year ==(25.77+54.19+46.18+28.4+25.3+32.43+67.53+72.83+

+71.96+71.07+55.04+41.75)×30=15998.1 m3 / year

Total energy  from pv system

Eh*365=2635.2 kwh/year

1 wp  --------------2.5$

3230wp  ------------?

3230 $ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost=8075+2000+1200+420 =11695 $

Annual fixed cost = .1 *capital cost         = .1* 11695=1169.5 $

Maintenance cost = .025* capital cost = .025* 1169.5= 292.375 $/year

Total annual cost= total fixed cost + total running cost

=292.375+1169.5=1461.875 $/year

Cost of (1kwh)= total annual cost /total energy =1461.875/2635.2=.5547$/year

$/m3 = total annual cost/ total pumping rate =1461.875/15998.1 =.091 $/m3

7 - 160 m3 / day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2inch.

Output of the well = 13  m3/ hour   for  12 hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =13  ×12=160 m3

Eh =0.002725×V × hT

=0.002725×160×56= 24.416kwh / day

E p in  =24.416/.0.55 =44.39 kwh /day .

E ASM in =44.39/0.82 = 54.13  Kwh / day  .

E inv in =54.13/0.92 =58.84 kwh / day .

Psh =5.4 kwh /day.

1kwp       →5.4 kwh /day.

?       →58.84 kwh / day.

PPV= 10.89 kwp .

January

E pv out = 2.85 ×10.89 =31.04 kwh / day

58.84 kwh / day    →160 m3 / day

31.04 kwh / day        →     ?

Average value of daily pumping water during January =84.4 m3 / day.

February

Epv out = 3.23 ×10.89 =34.84 kwh / day

58.84 kwh / day    →160 m3 / day

34.84 kwh / day        →     ?

Average value of daily pumping water during February =94.74 m3 / day.

March

Epv out = 3.23 ×10.89 =56.62 kwh/ day

58.84 kwh / day    →160 m3 / day

56.62 kwh / day        →     ?

Average value of daily pumping water during March   =153.96 m3 / day.

April

Epv out = 6.1 ×10.89 =66.42kwh / day

58.84 kwh / day    →160 m3 / day

66.42 kwh / day        →     ?

Average value of daily pumping water during   April  =180.6 m3 / day.

May

Epv out = 10.89 ×7.6 =82.76 kwh

58.84 kwh / day    →120 m3 / day

82.76 kwh / day        →     ?

Average value of daily pumping water during  May    =225 m3 / day.

June

Epv out = 10.89 ×8.2 =89.298 kwh

58.84kwh / day    →120 m3 / day

89.298kwh / day        →     ?

Average value of daily pumping water during   June  =242.8 m3 / day.

July

Epv out = 10.89 ×8.1 =88.209  kwh

58.84 kwh / day    →160 m3 / day

88.209 kwh / day        →     ?

Average value of daily pumping water during   July    =239.86 m3 / day.

August

Epv out = 10.89 ×8 =87.12  kwh

58.84 kwh / day    →160 m3 / day

87.12  kwh / day        →     ?

Average value of daily pumping water during   August  =236.9 m3 / day.

September

Epv out = 10.89 ×6.2 =67.518 kwh

58.84 kwh / day    →160 m3 / day

67.518 kwh / day        →     ?

Average value of daily pumping water during   September=183.59 m3 / day.

October

Epv out = 10.89 ×4.7 =51.18 kwh

58.84 kwh / day    →160 m3 / day

51.18 kwh / day        →     ?

Average value of daily pumping water during   October   =139.17 m3 / day.

November

Epv out = 10.89 ×3.65 =39.748 kwh

58.84 kwh / day    →160 m3 / day

39.748 kwh / day        →     ?

Average value of daily pumping water during   November  =108 m3 / day.

December

Epv out = 10.89 ×2.9=31.58 kwh .

58.84 kwh / day    →160 m3 / day

31.58 kwh / day        →     ?

Average value of daily pumping water during   December    =85.87 m3 / day.

Q year ==(34.84+94.74+153.96+180.6+225+242.8+239.86+236.9+

+183.59+139.17+108+85.87)×30=1925.33 m3 / year

Total energy  from pv system

Eh*365=8789.76 kwh/year

1 wp  --------------2.5$

10890wp  ------------?

27225 $ =cost of cells

Capital cost = cost cells+ cost inv+cost motor pupm + accessories cost

Capital cost= 27225+2700+4200+500 =34625 $

Annual fixed cost = .1 *capital cost         = .1* 34625=3462.5$

Maintenance cost = .025* capital cost = .025* 34625= 865.625 $/year

Total annual cost= total fixed cost + total running cost

= 3462.5+865.625=4328.125 $/year

Cost of (1kwh)= total annual cost /total energy =3462.5/8789.76=.39 $/year

$/m3 = total annual cost/ total pumping rate =3462.5/1925.33 =1.79  $/m3

9 -2 The  calculation of $/ m3 for diesel system

1 – 60 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =   5m3/ hour   for 12 hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =5*12=60

Eh =0.002725×V × hT

=0.002725×60×56= 9.156kwh / day

E p in  =(9.156 kwh /day)/.55 =16.65 kwh/day.

E ASM in  = (16.65  Kwh / day ) /.82= 20.3 kwh /day.

E S.G in   = 20.3/0.75 = 27.07 kwh

E DIESEL in =27.07/0.30 = 90.2 kwh

Number of liters diesel needed daily = 90.2/10.5 = 8.59

Diesel cost = 6* 8.59 NIS =51.56NIS/day  =12.89$/day

Diesel cost yearly = 12.86*365 =4704.85 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +1400+450 =4975 $

Total energy = Eh *365 = 3341.94 kwh/year

6 liters diesel ------------------------------ 1 liter oil

8.59 liters diesel ------------------------------ ? liter oil

We need 1.43 liters oil

Cost oil = 1.43 *5 =7.15 NIS  -----1.79 $

Cost oil yearly = 1.79*365= 6103.54 $/year

Annual fixed cost = .1 *capital cost         = .1* 4975=497.5$

Maintenance cost = .15 * capital cost = .15* 4975 = 746.25 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 4704.85+652.44+746.25 = 6103.54 $/year

Total annual cost= total fixed cost + total running cost

= 497.5 +6103.54 =6610.04 $/year

Cost of (1kwh)= total annual cost /total energy =6601.04/3341.94=1.98 $/year

$/m3 = total annual cost/ total pumping rate = 6601.04/(60*365) =0.301 $/m3

2- 120 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =  10 m3/ hour   for12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =120

Eh =0.002725×V × hT

=0.002725×120×56= 18.312kwh / day

E p in  =(18.312 kwh /day)/.55 =33.29 kwh/day.

E ASM in  = (33.29  Kwh / day ) /.82= 40.603 kwh /day.

E S.G in   = 40.603/0.75 = 54.14 kwh

E DIESEL in =54.14/0.30 = 180.46 kwh

Number of liters diesel needed daily = 180.46/10.5 = 17.19

Diesel cost = 6* 17.19 NIS =103.12NIS/day  =25.8$/day

Diesel cost yearly = 25.8*365 =9409.6 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +2200+500 =5825 $

Total energy = Eh *365 = 2175.84 kwh/year

6 liters diesel ------------------------------ 1 liter oil

17.19 liters diesel ------------------------------ ? liter oil

We need 2.865 liters oil

Cost oil = 2.865 *5 =14.325 NIS -----3.58 $

Cost oil yearly = 3.58*365= 1306.7 $/year

Annual fixed cost = .1 *capital cost         = .1*5825=582.5$

Maintenance cost = .15 * capital cost = .15* 5825 = 875.78 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 9409.6+873.78+1306.7 = 11590.08 $/year

Total annual cost= total fixed cost + total running cost

= 582.78 +11590.08 =12172.86 $/year

Cost of (1kwh)= total annual cost /total energy =

12172.86 /2175.84=5.59 $/year

$/m3 = total annual cost/ total pumping rate =

12172.86/ (120*365) =.2779 $/m3

3 - 80 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =  6.7 m3/ hour   for 12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =80

Eh =0.002725×V × hT

=0.002725×80×56= 12.208kwh / day

E p in  =(12.208 kwh /day)/.55 =22.2 kwh/day.

E ASM in  = (22.2  Kwh / day ) /.82= 27.068 kwh /day.

E S.G in   = 27.068/0.75 = 36.09 kwh

E DIESEL in =36.09/0.30 = 120.3 kwh

Number of liters diesel needed daily = 120.3/10.5 = 11.46

Diesel cost = 6* 11.46 NIS =68.76NIS/day  =17.19$/day

Diesel cost yearly = 17.19*365 =6274.35 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +1600+500 =5225$

Total energy = Eh *365 = 4455.92 kwh/year

6 liters diesel ------------------------------ 1 liter oil

11.46 liters diesel ------------------------------ ? liter oil

We need 1.91 liters oil

Cost oil = 1.91 *5 =9.55 NIS -----2.388 $

Cost oil yearly = 2.388*365= 871.44$/year

Annual fixed cost = .1 *capital cost         = .1*5225=522.5$

Maintenance cost = .15 * capital cost = .15* 5225 = 783.75 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 6274.35+783.75+871.94 = 7929.54 $/year

Total annual cost= total fixed cost + total running cost

= 522.5 +7929.54 =8452.04 $/year

Cost of (1kwh)= total annual cost /total energy =

8452.04 /4455.92=1.89 $/year

$/m3 = total annual cost/ total pumping rate =

8452.04/ (80*365) =.29 $/m3

4 - 20 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =  1.67 m3/ hour   for 12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =20

Eh =0.002725×V × hT

=0.002725×20×56= 3.052 kwh / day

E p in  =3.052/.55 =5.55 kwh/day.

E ASM in  = 5.55 /.82=6.77 kwh /day.

E S.G in   = 6.77/.75=9.02 kwh

E DIESEL in =9.02/0.30 = 30.06 kwh

Number of liters diesel needed daily = 30.06/10.5 =2.86

Diesel cost = 6* 2.86 NIS =17.16NIS/day  =4.29 $/day

Diesel cost yearly = 4.29*365 =1544.4 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +600+350 =4075 $

Total energy = Eh *365 = 1113.98 kwh/year

6 liters diesel ------------------------------ 1 liter oil

17.16 liters diesel ------------------------------ ? liter oil

We need 2.86 liters oil

Cost oil = 2.86 *5 =14.3 NIS -----3.575 $

Cost oil yearly = 3.575*365= 1304.875 $/year

Annual fixed cost = .1 *capital cost   = .1*4075=407.5 $

Maintenance cost = .15 * capital cost = .15* 4075 =611.25 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 1544.4+2017.5+611.25 =4173.15 $/year

Total annual cost= total fixed cost + total running cost

= 4173.15 +407.5 =4580.65 $/year

Cost of (1kwh)= total annual cost /total energy =

4580.65 /1113.98=4.1 $/year

$/m3 = total annual cost/ total pumping rate =

4580.65/ 20*365) =.62 $/m3

5 - 35 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well =  3 m3/ hour   for 12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day = 35 m3/ day

Eh =0.002725×V × hT

=0.002725×35×56=5.341kwh / day

E p in  =5.341/.55 =9.7 kwh/day.

E ASM in  = 9.7 /.82=11.83 kwh /day.

E S.G in   = 11.83/0.75 = 15.773 kwh

E DIESEL in =15.773/0.30 = 52.576 kwh

Number of liters diesel needed daily = 52.576/10.5 = 5 liter

Diesel cost = 6*5 NIS =30 NIS/day  = 7.5 $/day

Diesel cost yearly = 7.5*365 =2700 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +1000+400 =4525 $

Total energy = Eh *365 = 1949.465 kwh/year

6 liters diesel ------------------------------ 1 liter oil

5 liters diesel ------------------------------ ? liter oil

We need .83 liters oil

Cost oil = .83 *5 =4.15 NIS -----1.0375 $

Cost oil yearly = 1.0375*365= 373.5$/year

Annual fixed cost = .1 *capital cost         = .1*4525= 452.5 $

Maintenance cost = .15 * capital cost = .15* 4525 = 678.75  $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 2700+678.75+373.5 = 3752.25 $/year

Total annual cost= total fixed cost + total running cost

= 3752.25 +452.5 =4204.75 $/year

Cost of (1kwh)= total annual cost /total energy =

4204.75 /1049.465=2.1 $/year

$/m3 = total annual cost/ total pumping rate =

4204.75/ (35*365) =.329 $/m3

6- 48 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well = 4 m3/ hour   for 12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =48

Eh =0.002725×V × hT

=0.002725×48×56= 7.32kwh / day

E p in  7.32/.55 =13.3 kwh/day.

E ASM in  = 13.3 /.82= 16.23 kwh /day.

E S.G in   =16.23/0.75 =21.64 kwh

E DIESEL in =21.64/0.30 = 72.1 kwh

Number of liters diesel needed daily = 72.1/10.5 =6.86

Diesel cost = 6* 6.86 NIS =41.16NIS/day  =35.29 $/day

Diesel cost yearly = 35.29*365 = 3755.85 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 +1200+420 =4745 $

Total energy = Eh *365 = 2635.2  kwh/year

6 liters diesel ------------------------------ 1 liter oil

6.86 liters diesel ------------------------------ ? liter oil

We need 1.143 liters oil

Cost oil = 1.143 *5 =5.175 NIS -----1.428 $

Cost oil yearly = 1.428*365=521.64 $/year

Annual fixed cost = .1 *capital cost         = .1*4745=474.5 $

Maintenance cost = .15 * capital cost = .15* 4745 = 711.75 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 3755.85+711.75+521.64 = 4989.24 $/year

Total annual cost= total fixed cost + total running cost

= 4989.63 +474.5 =5463.74 $/year

Cost of (1kwh)= total annual cost /total energy =

5463.74 /2635.2=2.07 $/year

$/m3 = total annual cost/ total pumping rate =

5463.74/ (4880*365) =.31 $/m3

7 - 160 m3/ day

Well depth=60m.

Swl = 30m.

Dwl = 50m.

Pipe = 2 inch.

Output of the well = 13 m3/ hour   for 12  hour / day .

Total pumping head  (hT) = 50 +(6m) = 56m.

Total water capacity needed per day =160 m3/day

Eh =0.002725×V × hT

=0.002725×160×56= 24.416 kwh / day

E p in  24.461/.55 =44.39 kwh/day.

E ASM in  = 44.39 /.82= 54.13 kwh /day.

E S.G in   =54.13/0.75 =72.173 kwh

E DIESEL in =72.173/0.30 = 240.57 kwh

Number of liters diesel needed daily = 240.57/10.5 =22.91

Diesel cost = 6* 22.91 NIS =22.91NIS/day  =137.47 $/day

Diesel cost yearly = 137.47*365 = 50177.4 $/year

Capital cost = (12500/4) + (pumping cost) + (accessories cost)

3125 + 4200+500 =7825 $

Total energy = Eh *365 = 8911.84  kwh/year

6 liters diesel ------------------------------ 1 liter oil

22.91 liters diesel ------------------------------ ? liter oil

We need 3.8 liters oil

Cost oil = 3.8 *5 =19 NIS -----4.75 $

Cost oil yearly = 4.75*365=173.375 $/year

Annual fixed cost = .1 *capital cost         = .1*7825=782.5 $

Maintenance cost = .15 * capital cost = .15* 7825 = 1173.75 $/year

Annual running cost =diesel cost +maintenance cost+ oil cost

= 5177.4+1173.75+173.375 =10430.3 $/year

Total annual cost= total fixed cost + total running cost

= 782.5 +10430.3 =11212.8 $/year

Cost of (1kwh)= total annual cost /total energy =

11212.8 /8911.84=1.25 $/year

$/m3 = total annual cost/ total pumping rate =

11212.8/ (160*365) =.192 $/m3